## Logano G115-215-315-515-615
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano G115 WS - 215 WS - GE315 - GE515 - GE615
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano G115 WS | 25 | 21500 | 27.3 | 0.11 | Max Gas 40 | P | ------ | ------ | TC - SHORT | Max 1 | Av. | ------ | ------ | TC - SHORT | ------------- | ------ | ------ | ------ | TC - SHORT
Logano G115 WS | 32 | 27520 | 34.9 | 0.11 | Max Gas 40 | P | ------ | ------ | TC - SHORT | Max 1 | Av. | ------ | ------ | TC - SHORT | ------------- | ------ | ------ | ------ | TC - SHORT
Logano G115 WS | 40 | 34400 | 43.6 | 0.16 | Max Gas 40 | P | ------ | ------ | TC - SHORT | Max 1 | Av. | ------ | ------ | TC - SHORT | ------------- | ------ | ------ | ------ | TC - SHORT
Logano G215 WS | 52 | 44720 | 56.6 | 0.42 | Max Gas 70 | P | PAB | PR * | TC - SHORT | MAX 4 | Av. | ------ | ------ | TC - SHORT | ------------- | ------ | ------ | ------ | TC - SHORT
Logano G215 WS | 64 | 55040 | 65.3 | 0.35 | Max Gas 70 | P | PAB | PR * | TC - SHORT | MAX 8 | Av. | ------ | ------ | TC - SHORT | ------------- | ------ | ------ | ------ | TC - SHORT
Logano G215 WS | 78 | 67080 | 85.1 | 0.46 | Max Gas 105 | P | PAB | PR * | TC - SHORT | MAX 8 | Av. | ------ | ------ | TC - SHORT | ------------- | ------ | ------ | ------ | TC - SHORT
Logano G215 WS | 95 | 81700 | 103.2 | 0.71 | Max Gas 105 | P | PAB | PR * | TC - SHORT | MAX 12 | Av. | ------ | ------ | TC - SHORT | ------------- | ------ | ------ | ------ | TC - SHORT
Logano GE315 | 105 | 90300 | 113.5 | 0.41 | Max Gas 120 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | ------ | PAB | PR * | TC - SHORT
Logano GE315 | 140 | 120400 | 151.4 | 0.79 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | ------ | PAB | PR * | TC - SHORT
Logano GE315 | 170 | 146200 | 183.4 | 1.3 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 4 P | ------ | PAB | PR * | TC - SHORT
Logano GE315 | 200 | 172000 | 215.1 | 1.78 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
Logano GE315 | 230 | 197800 | 230 | 1.77 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 240 | 206400 | 259.7 | 0.6 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | ------ | PAB | PR * | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 295 | 253700 | 319 | 1.4 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 350 | 301000 | 377 | 1.6 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 400 | 344000 | 429.6 | 2.9 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 455 | 391300 | 489.2 | 3.3 | Blu 500 | ------ | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 510 | 438600 | 547.8 | 3.1 | Blu 700 | ------ | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 570 | 490200 | 616.2 | 2.4 | Blu 700 | ------ | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 660 | 567600 | 713.5 | 3.4 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 740 | 636400 | 800 | 4.2 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 820 | 705200 | 886.5 | 4.2 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 920 | 791200 | 994.6 | 4.1 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 1020 | 877200 | 1102 | 4.5 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 1110 | 954600 | 1200 | 5.4 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 1200 | 1032000 | 1297 | 5.8 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano GE315 - GE515 - GE615
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano GE315 | 105 | 90300 | 113.5 | 0.41 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano GE315 | 140 | 120400 | 151.4 | 0.79 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano GE315 | 170 | 146200 | 183.4 | 1.3 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano GE315 | 200 | 172000 | 215.1 | 1.78 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano GE315 | 230 | 197800 | 230 | 1.77 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano GE515 | 240 | 206400 | 259.7 | 0.6 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano GE515 | 295 | 253700 | 319 | 1.4 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano GE515 | 350 | 301000 | 377 | 1.6 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 400 | 344000 | 429.6 | 2.9 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 455 | 391300 | 489.2 | 3.3 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
Logano GE515 | 510 | 438600 | 547.8 | 3.1 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 570 | 490200 | 616.2 | 2.4 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 660 | 567600 | 713.5 | 3.4 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 740 | 636400 | 800 | 4.2 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 820 | 705200 | 886.5 | 4.2 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 920 | 791200 | 994.6 | 4.1 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 1020 | 877200 | 1102 | 4.5 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 1110 | 954600 | 1200 | 5.4 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
Logano GE615 | 1200 | 1032000 | 1297 | 5.8 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## Logano SE425-635-735
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano SE425 - SE635 - SE735
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano SE425 | 80 | 68800 | 86.6 | 0.44 | Max Gas 105 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 3 P | P | ------ | ------ | TC - SHORT
Logano SE425 | 110 | 94600 | 118.9 | 0.58 | Max Gas 120 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
Logano SE425 | 140 | 120400 | 151.4 | 1.06 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
Logano SE425 | 170 | 146200 | 183.6 | 1.16 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
Logano SE635 | 230 | 197800 | 250 | 2.3 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | ------ | PAB | PR * | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
Logano SE635 | 280 | 240800 | 304 | 2.9 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano SE635 | 350 | 301000 | 380 | 3.2 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano SE635 | 420 | 361200 | 457 | 3.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano SE635 | 490 | 421400 | 533 | 3.9 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 590 | 507400 | 641 | 4.4 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 730 | 627800 | 793 | 5 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 920 | 791200 | 1000 | 5.5 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 1120 | 963200 | 1217 | 6.4 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 1400 | 1204000 | 1522 | 6.6 | Blu 1700.1 | ------ | PAB | PR * | TC - SHORT | Maior P 200.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 1750 | 1505000 | 1902 | 7.5 | Blu 2000.1 | ------ | PAB | PR * | TC - SHORT | Maior P 200.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano SE425 - SE635 - SE735
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano SE425 | 80 | 68800 | 86.6 | 0.44 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SE425 | 110 | 94600 | 118.9 | 0.58 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SE425 | 140 | 120400 | 151.4 | 1.06 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SE425 | 170 | 146200 | 183.6 | 1.16 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SE635 | 230 | 197800 | 250 | 2.3 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SE635 | 280 | 240800 | 304 | 2.9 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SE635 | 350 | 301000 | 380 | 3.2 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
Logano SE635 | 420 | 361200 | 457 | 3.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
Logano SE635 | 490 | 421400 | 533 | 3.9 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 80.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 590 | 507400 | 641 | 4.4 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 80.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 730 | 627800 | 793 | 5 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 920 | 791200 | 1000 | 5.5 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 1120 | 963200 | 1217 | 6.4 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 1400 | 1204000 | 1522 | 6.6 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
Logano SE735 | 1750 | 1505000 | 1902 | 7.5 | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## Logano SK425-625-735
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano SK425 - SK625 - SK725
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano SK425 | 90 | 77400 | 97.3 | 0.5 | Max Gas 105 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 3 P | P | ------ | ------ | TC - SHORT
Logano SK425 | 120 | 103200 | 129.7 | 0.9 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
Logano SK425 | 150 | 129000 | 162.2 | 1.3 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
Logano SK425 | 180 | 154800 | 194.6 | 1.6 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
Logano SK625 | 230 | 197800 | 249 | 2 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | ------ | PAB | PR * | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
Logano SK625 | 310 | 266600 | 335 | 2.35 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano SK625 | 410 | 352600 | 443 | 3 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
Logano SK625 | 530 | 455800 | 573 | 3.35 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
Logano SK625 | 690 | 593400 | 746 | 4.05 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 870 | 748200 | 940.5 | 4.85 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 1070 | 920200 | 1156.8 | 5.69 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 1320 | 1135200 | 1427 | 5.87 | Blu 1700.1 | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 1600 | 1376000 | 1729.7 | 6.05 | Blu 2000.1 | ------ | PAB | PR * | TC - SHORT | Maior P 200.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano SK425 - SK625 - SK725
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano SK425 | 90 | 77400 | 97.3 | 0.5 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SK425 | 120 | 103200 | 129.7 | 0.9 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SK425 | 150 | 129000 | 162.2 | 1.3 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SK425 | 180 | 154800 | 194.6 | 1.6 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SK625 | 230 | 197800 | 249 | 2 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SK625 | 310 | 266600 | 335 | 2.35 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | ---------- | ------ | ------ | ------ | ------
Logano SK625 | 410 | 352600 | 443 | 3 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
Logano SK625 | 530 | 455800 | 573 | 3.35 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
Logano SK625 | 690 | 593400 | 746 | 4.05 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 870 | 748200 | 940.5 | 4.85 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 1070 | 920200 | 1156.8 | 5.69 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 1320 | 1135200 | 1427 | 5.87 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
Logano SK725 | 1600 | 1376000 | 1729.7 | 6.05 | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## Logano S825L
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano S825L
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano S825L | 650 | 559000
Logano S825L | 1000 | 860000
Logano S825L | 1350 | 1161000
Logano S825L | 1900 | 1634000
Logano S825L | 2500 | 2150000
Logano S825L | 3050 | 2623000
Logano S825L | 3700 | 3182000
Logano S825L | 4150 | 3569000
Logano S825L | 5200 | 4472000
Logano S825L | 6500 | 5590000
Logano S825L | 7700 | 6622000
Logano S825L | 9300 | 7998000
Logano S825L | 11200 | 9632000
Logano S825L | 12600 | 10836000
Logano S825L | 14700 | 12642000
Logano S825L | 16400 | 14104000
Logano S825L | 19200 | 16512000
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano SK425 - SK625 - SK725
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano S825L | 650 | 559000
Logano S825L | 1000 | 860000
Logano S825L | 1350 | 1161000
Logano S825L | 1900 | 1634000
Logano S825L | 2500 | 2150000
Logano S825L | 3050 | 2623000
Logano S825L | 3700 | 3182000
Logano S825L | 4150 | 3569000
Logano S825L | 5200 | 4472000
Logano S825L | 6500 | 5590000
Logano S825L | 7700 | 6622000
Logano S825L | 9300 | 7998000
Logano S825L | 11200 | 9632000
Logano S825L | 12600 | 10836000
Logano S825L | 14700 | 12642000
Logano S825L | 16400 | 14104000
Logano S825L | 19200 | 16512000
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## Logano S825LN
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano S825L
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano S825LN | 500 | 430000
Logano S825LN | 750 | 645000
Logano S825LN | 100 | 86000
Logano S825LN | 1500 | 1290000
Logano S825LN | 2000 | 1720000
Logano S825LN | 2500 | 2150000
Logano S825LN | 3000 | 2580000
Logano S825LN | 3500 | 3010000
Logano S825LN | 4250 | 3655000
Logano S825LN | 5250 | 4515000
Logano S825LN | 6000 | 5160000
Logano S825LN | 8000 | 6880000
Logano S825LN | 10000 | 8600000
Logano S825LN | 12000 | 10320000
Logano S825LN | 14000 | 12040000
Logano S825LN | 17500 | 15050000
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: BUDERUS - Logano SK425 - SK625 - SK725
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Logano S825LN | 500 | 430000
Logano S825LN | 750 | 645000
Logano S825LN | 100 | 86000
Logano S825LN | 1500 | 1290000
Logano S825LN | 2000 | 1720000
Logano S825LN | 2500 | 2150000
Logano S825LN | 3000 | 2580000
Logano S825LN | 3500 | 3010000
Logano S825LN | 4250 | 3655000
Logano S825LN | 5250 | 4515000
Logano S825LN | 6000 | 5160000
Logano S825LN | 8000 | 6880000
Logano S825LN | 10000 | 8600000
Logano S825LN | 12000 | 10320000
Logano S825LN | 14000 | 12040000
Logano S825LN | 17500 | 15050000
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE