## GN
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli GN 1K - GN 1 - GN 2 N - GN 4 N
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNERS VERSION |  |  |  | BLAST TUBE LENGTH | LIGHT OIL BURNERS VERSION
[5 empty] | TYPE | ON - OFF | HI - LOW | PR-MD | TC - TL |  | ON - OFF | HI - LOW | PR-MD
GN 1K N 01 | 23.3 | 20038 | 25.8 | 0.2 | MAX GAS 40 | P | ---------- | ------ | TC - SHORT | Max 1 | Av. | ---------- | ------
GN 1K N 02 | 31.4 | 27004 | 34.8 | 0.2 | MAX GAS 40 | P | PAB | ------ | TC - SHORT | Max 1 | Av. | ---------- | ------
GN 1K N 03 | 46.5 | 39990 | 51.6 | 0.2 | MAX GAS 70 | P | PAB | ------ | TC - SHORT | Max 4 | Av. | ---------- | ------
GN 1.02 | 23.3 | 20038 | 25.8 | 0.2 | MAX GAS 40 | P | PAB | ------ | TC - SHORT | Max 1 | Av. | ---------- | ------
GN 1.03 | 31.4 | 27004 | 34.8 | 0.2 | MAX GAS 40 | P | PAB | ------ | TC - SHORT | Max 1 | Av. | ---------- | ------
GN 1.04 | 46.5 | 39990 | 51.6 | 0.2 | MAX GAS 70 | P | PAB | ------ | TC - SHORT | Max 4 | Av. | ---------- | ------
GN 1.05 | 58.1 | 49966 | 64.5 | 0.2 | MAX GAS 70 | P | PAB | ------ | TC - SHORT | Max 8 | Av. | ---------- | ------
GN 1.06 | 69.8 | 60028 | 77.5 | 0.2 | MAX GAS 105 | P | PAB | PR * | TC - SHORT | Max 8 | Av. | ---------- | ------
GN 1.07 | 81.4 | 70004 | 90.4 | 0.2 | MAX GAS 105 | P | PAB | PR * | TC - SHORT | Max 8 | Av. | ---------- | ------
GN 1.08 | 93 | 79980 | 103.3 | 0.2 | MAX GAS 120 | P | PAB | PR * | TC - SHORT | Max 8 | Av. | ---------- | ------
GN 2 N 06 | 107 | 92020 | 116 | 0.4 | MAX GAS 170 | P | PAB | PR * | TC - SHORT | Max 12 | Av. | ---------- | ------
GN 2 N 07 | 126 | 108360 | 136.9 | 0.4 | MAX GAS 170 | P | PAB | PR * | TC - SHORT | Max 15 | Av. | PAB | ------
GN 2 N 08 | 144 | 123840 | 156.5 | 0.4 | MAX GAS 170 | P | PAB | PR * | TC - SHORT | Max 15 | Av. | PAB | ------
GN 2 N 09 | 162 | 139320 | 176 | 0.4 | MAX GAS 250 | P | PAB | PR * | TC - SHORT | Max 15 | Av. | PAB | ------
GN 2 N 10 | 180 | 154800 | 195.6 | 0.4 | MAX GAS 250 | P | PAB | PR * | TC - SHORT | Max 20 | Av. | PAB | ------
GN 2 N 11 | 198 | 170280 | 215.2 | 0.4 | MAX GAS 250 | P | PAB | PR * | TC - SHORT | Max 20 | Av. | PAB | ------
GN 2 N 12 | 216 | 185760 | 234.7 | 0.4 | MAX GAS 250 | P | PAB | PR * | TC - SHORT | Max 20 | Av. | PAB | ------
GN 2 N 13 | 234 | 201240 | 254.3 | 0.4 | Blu 350 | P | PAB | PR * | TC - SHORT | Max 30 | Av. | PAB | ------
GN 2 N 14 | 252 | 216720 | 273.9 | 0.4 | Blu 350 | P | PAB | PR * | TC - SHORT | Max 30 | Av. | PAB | ------
GN 4 N 07 | 200 | 172000 | 217 | 0.5 | MAX GAS 250 | P | PAB | PR * | TC - SHORT | Max 20 | Av. | PAB | ------
GN 4 N 08 | 250 | 215000 | 270 | 0.8 | Blu 350 | P | PAB | PR * | TC - SHORT | Max P 25 | P | PAB | ------
GN 4 N 09 | 300 | 258000 | 324 | 0.7 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | PAB | ------
GN 4 N 10 | 360 | 309600 | 388 | 1 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR *
GN 4 N 11 | 420 | 361200 | 452 | 1.4 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR *
GN 4 N 12 | 480 | 412800 | 516 | 1.7 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR *
GN 4 N 13 | 560 | 481600 | 600 | 2.6 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR *
GN 4 N 14 | 650 | 559000 | 695 | 3.5 | Blu 1000 | P | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR *
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## Prextherm RSW - NGT
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli Prextherm RSW - NGT
TYPE |  | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[6 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Prextherm RSW 92 | NGT 92 | 92 | 79120 | 99.5 | 0.5 | MAX GAS 120 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ---- | TL - LONG | DUAL 4 P | P | ---- | ---- | TL - LONG
Prextherm RSW 107 | NGT 107 | 107 | 92020 | 116 | 0.7 | MAX GAS 120 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ---- | TL - LONG | DUAL 4 P | P | ---- | ---- | TL - LONG
Prextherm RSW 152 | NGT 152 | 152 | 130720 | 165 | 1.2 | MAX GAS 170 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ---- | TL - LONG | DUAL 4 P | P | ---- | ---- | TL - LONG
Prextherm RSW 190 | NGT 190 | 190 | 163400 | 206 | 1.2 | MAX GAS 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ---- | TL - LONG | DUAL 5 P | P | ---- | ---- | TL - LONG
Prextherm RSW 240 | NGT 240 | 240 | 206400 | 261 | 2.3 | Blu 350 | P | PAB | PR * | TL - LONG | Maior 35 P | P | PAB | ---- | TL - LONG | DUAL 5 P | P | ---- | ---- | TL - LONG
Prextherm RSW 300 | NGT 300 | 300 | 258000 | 326 | 3.3 | Blu 500 | P | PAB | PR * | TL - LONG | Maior 45 | P | PAB | ---- | TL - LONG | DUAL 5 P | P | ---- | ---- | TL - LONG
Prextherm RSW 350 | NGT 350 | 350 | 301000 | 378 | 4.4 | Blu 500 | P | PAB | PR * | TL - LONG | Maior 45 | ---- | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 399 | NGT 399 | 399 | 343140 | 432 | 4.4 | Blu 500 | P | PAB | PR * | TL - LONG | Maior 60 | ---- | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 469 | NGT 469 | 469 | 403340 | 507 | 3.3 | Blu 700 | P | PAB | PR * | TL - LONG | Maior 60 | ---- | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 525 | NGT 525 | 525 | 451500 | 567 | 4.3 | Blu 700 | P | PAB | PR * | TL - LONG | Maior 60 | ---- | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 600 | NGT 600 | 600 | 516000 | 648 | 4.8 | Blu 1000 | ---- | PAB | PR * | TL - LONG | Maior 80 | ---- | PAB | PR * | TL - LONG | Multicalor 100 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 720 | NGT 720 | 720 | 619200 | 781 | 4.5 | Blu 1000 | ---- | PAB | PR * | TL - LONG | Maior 80 | ---- | PAB | PR * | TL - LONG | Multicalor 100 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 820 | NGT 820 | 820 | 705200 | 881 | 5.6 | Blu 1400 | ---- | PAB | PR * | TL - LONG | Maior 120 | ---- | PAB | PR * | TL - LONG | Multicalor 140 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 940 | NGT 940 | 940 | 808400 | 1014 | 5.4 | Blu 1400 | ---- | PAB | PR * | TL - LONG | Maior 120 | ---- | PAB | PR * | TL - LONG | Multicalor 140 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1060 | NGT 1060 | 1060 | 911600 | 1140 | 6 | Blu 1700.1 R | ---- | PAB | PR * | TL - LONG | Maior 120 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1250 | NGT 1250 | 1250 | 1075000 | 1359 | 6.5 | Blu 1700.1 | ---- | PAB | PR * | TL - LONG | Maior 150.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1480 | NGT 1480 | 1480 | 1272800 | 1608 | 6.8 | Blu 2000.1 | ---- | PAB | PR * | TL - LONG | Maior 200.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1890 | NGT 1890 | 1890 | 1625400 | 2054 | 7 | Blu 3000.1 | ---- | PAB | PR * | TL - LONG | Maior 200.1 | ---- | PAB | PR * | TL - LONG | Multicalor 200.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 2360 | NGT 2360 | 2360 | 2029600 | 2565 | 7.2 | Blu 3000.1 | ---- | PAB | PR * | TL - LONG | Maior 300.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 3000 | NGT 3000 | 3000 | 2580000 | 3260 | 7.5 | Blu 4000.1 | ---- | PAB | PR * | TL - LONG | Maior 400.1 | ---- | PAB | PR * | TL - LONG | Multicalor 400.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 3600 | NGT 3600 | 3600 | 3096000 | 3913 | 7.8 | Blu 5000.1 | ---- | PAB | PR * | TL - LONG | Maior 500.1 | ---- | PAB | PR * | TL - LONG | Multicalor 500.1 | ---- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli Prextherm RSW - NGT
TYPE |  | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[6 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Prextherm RSW 92 | NGT 92 | 92 | 79120 | 99.5 | 0.5 | Oilflam 15.1 | P | ---- | ---- | TL - LONG | Oilflam 15.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
Prextherm RSW 107 | NGT 107 | 107 | 92020 | 116 | 0.7 | Oilflam 15.1 | P | ---- | ---- | TL - LONG | Oilflam 15.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
Prextherm RSW 152 | NGT 152 | 152 | 130720 | 165 | 1.2 | Oilflam 15.1 | P | ---- | ---- | TL - LONG | Oilflam 15.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
Prextherm RSW 190 | NGT 190 | 190 | 163400 | 206 | 1.2 | Oilflam 20.1 | P | ---- | ---- | TL - LONG | Oilflam 20.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
Prextherm RSW 240 | NGT 240 | 240 | 206400 | 261 | 2.3 | Oilflam 30.1 | P | ---- | ---- | TL - LONG | Oilflam 30.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
Prextherm RSW 300 | NGT 300 | 300 | 258000 | 326 | 3.3 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
Prextherm RSW 350 | NGT 350 | 350 | 301000 | 378 | 4.4 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 50 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 399 | NGT 399 | 399 | 343140 | 432 | 4.4 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 50 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 469 | NGT 469 | 469 | 403340 | 507 | 3.3 | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Multiflam 70 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 525 | NGT 525 | 525 | 451500 | 567 | 4.3 | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Multiflam 70 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 600 | NGT 600 | 600 | 516000 | 648 | 4.8 | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Multiflam 70 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 720 | NGT 720 | 720 | 619200 | 781 | 4.5 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 820 | NGT 820 | 820 | 705200 | 881 | 5.6 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 940 | NGT 940 | 940 | 808400 | 1014 | 5.4 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1060 | NGT 1060 | 1060 | 911600 | 1140 | 6 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1250 | NGT 1250 | 1250 | 1075000 | 1359 | 6.5 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1480 | NGT 1480 | 1480 | 1272800 | 1608 | 6.8 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 200.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 1890 | NGT 1890 | 1890 | 1625400 | 2054 | 7 | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 2360 | NGT 2360 | 2360 | 2029600 | 2565 | 7.2 | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 3000 | NGT 3000 | 3000 | 2580000 | 3260 | 7.5 | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Multiflam 400.1 | ---- | PAB | PR * | TL - LONG
Prextherm RSW 3600 | NGT 3600 | 3600 | 3096000 | 3913 | 7.8 | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Multiflam 500.1 | ---- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## Prextherm T 3G
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli Prextherm T 3G
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Prextherm T 3G 1200 | 1200 | 1032000 | 1297 | 4.5 | Blu 1700.1 R | ---- | PAB | PR * | TL - LONG | Maior 150.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 1400 | 1400 | 1204000 | 1513 | 6.3 | Blu 1700.1 | ---- | PAB | PR * | TL - LONG | Maior 150.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 1750 | 1760 | 1513600 | 1902 | 5.5 | Blu 2000.1 | ---- | PAB | PR * | TL - LONG | Maior 200.1 | ---- | PAB | PR * | TL - LONG | Multicalor 200.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 2000 | 2000 | 1720000 | 2162 | 7.4 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior 300.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 2300 | 2300 | 1978000 | 2500 | 4 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior 300.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 2800 | 2800 | 2408000 | 3027 | 5.2 | Blu 4000.1 | ---- | ---- | PR * | TL - LONG | Maior 400.1 | ---- | PAB | PR * | TL - LONG | Multicalor 400.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 3400 | 3400 | 2924000 | 3700 | 6.1 | Blu 5000.1 | ---- | ---- | PR * | TL - LONG | Maior 500.1 | ---- | PAB | PR * | TL - LONG | Multicalor 500.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 4000 | 4000 | 3440000 | 4345 | 5.4 | Blu 6000.1 | ---- | ---- | PR * | TL - LONG | Maior 600.1 | ---- | PAB | PR * | TL - LONG | Multicalor 600.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 4600 | 4600 | 3956000 | 5000 | 7.5 | Blu 6000.1 | ---- | ---- | PR * | TL - LONG | Maior 600.1 | ---- | PAB | PR * | TL - LONG | Multicalor 600.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 5200 | 5200 | 4472000 | 5653 | 8.2 | Blu 7000.1 | ---- | ---- | PR * | STD. | Maior 700.1 | ---- | ---- | PR * | STD. | Multicalor 700.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 6000 | 6000 | 5160000 | 6522 | 6.1 | Blu 7000.1 | ---- | ---- | PR * | STD. | Maior 700.1 | ---- | ---- | PR * | STD. | Multicalor 700.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 7000 | 7000 | 6020000 | 7609 | 8.4 | Blu 8000.1 | ---- | ---- | PR * | STD. | Maior 800.1 | ---- | ---- | PR * | STD. | Multicalor 800.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 8000 | 8000 | 6880000 | 8697 | 8.2 | Blu 10000.1 | ---- | ---- | PR * | STD. | Maior 1000.1 | ---- | ---- | PR * | STD. | Multicalor 1000.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 9000 | 9000 | 7740000 | 9783 | 8.5 | Blu 10000.1 | ---- | ---- | PR * | STD. | Maior 1000.1 | ---- | ---- | PR * | STD. | Multicalor 1000.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 10000 | 10000 | 8600000 | 10870 | 8.7 | Blu 12000.1 | ---- | ---- | PR * | STD. | Maior 1200.1 | ---- | ---- | PR * | STD. | Multicalor 1200.1 | ---- | ---- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli Prextherm T 3G
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
Prextherm T 3G 1200 | 1200 | 1032000 | 1297 | 4.5 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 1400 | 1400 | 1204000 | 1513 | 6.3 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 1750 | 1760 | 1513600 | 1902 | 5.5 | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Multiflam 200.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 2000 | 2000 | 1720000 | 2162 | 7.4 | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 2300 | 2300 | 1978000 | 2500 | 4 | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 2800 | 2800 | 2408000 | 3027 | 5.2 | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Multiflam 400.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 3400 | 3400 | 2924000 | 3700 | 6.1 | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Multiflam 500.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 4000 | 4000 | 3440000 | 4345 | 5.4 | Oilflam 600.1 | ---- | PAB | PR * | TL - LONG | Oilflam 600.1 | ---- | PAB | PR * | TL - LONG | Multiflam 600.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 4600 | 4600 | 3956000 | 5000 | 7.5 | Oilflam 600.1 | ---- | ---- | PR * | TL - LONG | Oilflam 600.1 | ---- | PAB | PR * | TL - LONG | Multiflam 600.1 | ---- | PAB | PR * | TL - LONG
Prextherm T 3G 5200 | 5200 | 4472000 | 5653 | 8.2 | Oilflam 700.1 | ---- | ---- | PR * | STD. | Oilflam 700.1 | ---- | ---- | PR * | STD. | Multiflam 700.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 6000 | 6000 | 5160000 | 6522 | 6.1 | Oilflam 700.1 | ---- | ---- | PR * | STD. | Oilflam 700.1 | ---- | ---- | PR * | STD. | Multiflam 700.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 7000 | 7000 | 6020000 | 7609 | 8.4 | Oilflam 800.1 | ---- | ---- | PR * | STD. | Oilflam 800.1 | ---- | ---- | PR * | STD. | Multiflam 800.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 8000 | 8000 | 6880000 | 8697 | 8.2 | Oilflam 1000.1 | ---- | ---- | PR * | STD. | Oilflam 1000.1 | ---- | ---- | PR * | STD. | Multiflam 1000.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 9000 | 9000 | 7740000 | 9783 | 8.5 | Oilflam 1000.1 | ---- | ---- | PR * | STD. | Oilflam 1200.1 | ---- | ---- | PR * | STD. | Multiflam 1000.1 | ---- | ---- | PR * | STD.
Prextherm T 3G 10000 | 10000 | 8600000 | 10870 | 8.7 | Oilflam 1200.1 | ---- | ---- | PR * | STD. | Oilflam 1200.1 | ---- | ---- | PR * | STD. | Multiflam 1200.1 | ---- | ---- | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## Prex 3GN
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli Prex 3GN
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | LIGHT OIL BURNER
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
Prex 3GN 2000 | 2326 | 2000360 | 2584 | 4.5 | Blu 3000.1 | --- | PR * | TL - LONG | Maior P 300.1 | PAB | PR * | TL - LONG | Multicalor 300.1 | PAB | PR * | TL - LONG
Prex 3GN 2500 | 2907 | 2500020 | 3230 | 6.5 | Blu 4000.1 | --- | PR * | TL - LONG | Maior P 400.1 | PAB | PR * | TL - LONG | Multicalor 400.1 | PAB | PR * | TL - LONG
Prex 3GN 3000 | 3489 | 3000540 | 3876 | 5.1 | Blu 5000.1 | --- | PR * | TL - LONG | Maior P 500.1 | PAB | PR * | TL - LONG | Multicalor 500.1 | --- | PR * | TL - LONG
Prex 3GN 3500 | 4070 | 3500200 | 4522 | 7.2 | Blu 6000.1 | --- | PR * | TL - LONG | Maior P 600.1 | PAB | PR * | TL - LONG | Multicalor 600.1 | --- | PR * | TL - LONG
Prex 3GN 4000 | 4652 | 4000720 | 5168 | 6.5 | Blu 6000.1 | --- | PR * | TL - LONG | Maior P 600.1 | PAB | PR * | TL - LONG | Multicalor 600.1 | --- | PR * | TL - LONG
Prex 3GN 4500 | 5234 | 4501240 | 5815 | 8.4 | Blu 7000.1 | --- | PR * | STD. | Maior P 700.1 | --- | PR * | STD. | Multicalor 700.1 | --- | PR * | STD.
Prex 3GN 5000 | 5815 | 5000900 | 6461 | 6.5 | Blu 7000.1 | --- | PR * | STD. | Maior P 700.1 | --- | PR * | STD. | Multicalor 700.1 | --- | PR * | STD.
Prex 3GN 6000 | 6978 | 6001080 | 7753 | 8.7 | Blu 8000.1 | --- | PR * | STD. | Maior P 800.1 | --- | PR * | STD. | Multicalor 800.1 | --- | PR * | STD.
Prex 3GN 7200 | 8374 | 7201640 | 9304 | 7.5 | Blu 10000.1 | --- | PR * | STD. | Maior P 1000.1 | --- | PR * | STD. | Multicalor 1000.1 | --- | PR * | STD.
Prex 3GN 9000 | 10467 | 9001620 | 11630 | 9 | Blu 12000.1 | --- | PR * | STD. | Maior P 1200.1 | --- | PR * | STD. | Multicalor 1200.1 | --- | PR * | STD.
Prex 3GN 10000 | 11630 | 10001800 | 12922 | 12 | Blu 15000.1 | --- | PR * | STD. | Maior P 1500.1 | --- | PR * | STD. | Multicalor 1500.1 | --- | PR * | STD.
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
Prex 3GN 2000 | 2326 | 2000360 | 2584 | 4.5 | Oilflam 300.1 | --- | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam 300.1 | PAB | PR * | TL - LONG
Prex 3GN 2500 | 2907 | 2500020 | 3230 | 6.5 | Oilflam 400.1 | --- | PR * | TL - LONG | Oilflam 400.1 | PAB | PR * | TL - LONG | Multiflam 400.1 | PAB | PR * | TL - LONG
Prex 3GN 3000 | 3489 | 3000540 | 3876 | 5.1 | Oilflam 500.1 | --- | PR * | TL - LONG | Oilflam 500.1 | PAB | PR * | TL - LONG | Multiflam 500.1 | --- | PR * | TL - LONG
Prex 3GN 3500 | 4070 | 3500200 | 4522 | 7.2 | Oilflam 600.1 | --- | PR * | TL - LONG | Oilflam 600.1 | PAB | PR * | TL - LONG | Multiflam 600.1 | --- | PR * | TL - LONG
Prex 3GN 4000 | 4652 | 4000720 | 5168 | 6.5 | Oilflam 600.1 | --- | PR * | TL - LONG | Oilflam 600.1 | PAB | PR * | TL - LONG | Multiflam 600.1 | --- | PR * | TL - LONG
Prex 3GN 4500 | 5234 | 4501240 | 5815 | 8.4 | Oilflam 700.1 | --- | PR * | STD. | Oilflam 700.1 | --- | PR * | STD. | Multiflam 700.1 | --- | PR * | STD.
Prex 3GN 5000 | 5815 | 5000900 | 6461 | 6.5 | Oilflam 700.1 | --- | PR * | STD. | Oilflam 700.1 | --- | PR * | STD. | Multiflam 700.1 | --- | PR * | STD.
Prex 3GN 6000 | 6978 | 6001080 | 7753 | 8.7 | Oilflam 800.1 | --- | PR * | STD. | Oilflam 800.1 | --- | PR * | STD. | Multiflam 800.1 | --- | PR * | STD.
Prex 3GN 7200 | 8374 | 7201640 | 9304 | 7.5 | Oilflam 1000.1 | --- | PR * | STD. | Oilflam 1000.1 | --- | PR * | STD. | Multiflam 1000.1 | --- | PR * | STD.
Prex 3GN 9000 | 10467 | 9001620 | 11630 | 9 | Oilflam 1200.1 | --- | PR * | STD. | Oilflam 1200.1 | --- | PR * | STD. | Multiflam 1200.1 | --- | PR * | STD.
Prex 3GN 10000 | 11630 | 10001800 | 12922 | 12 | Oilflam 1500.1 | --- | PR * | STD. | Oilflam 1500.1 | --- | PR * | STD. | Multiflam 1500.1 | --- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## PREX 3G AS
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli PREX 3G ASL - ASH
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | LIGHT OIL BURNER
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
PREX 3G AS 1250 | 1454 | 1250440 | 1615 | 5.8 | Blu 1700.1 | PAB | PR * | TL - LONG | Maior P 200.1 | PAB | PR * | TL - LONG | Multicalor 200.1 | PAB | PR * | TL - LONG
PREX 3G AS 1500 | 1744 | 1499840 | 1937 | 7.1 | Blu 3000.1 | ---- | PR * | TL - LONG | Maior P 300.1 | PAB | PR * | TL - LONG | Multicalor 300.1 | PAB | PR * | TL - LONG
PREX 3G AS 1750 | 2034 | 1749240 | 2260 | 8.5 | Blu 3000.1 | ---- | PR * | TL - LONG | Maior P 300.1 | PAB | PR * | TL - LONG | Multicalor 300.1 | PAB | PR * | TL - LONG
PREX 3G AS 2000 | 2326 | 2000360 | 2584 | 10 | Blu 3000.1 | ---- | PR * | TL - LONG | Maior P 300.1 | PAB | PR * | TL - LONG | Multicalor 300.1 | PAB | PR * | TL - LONG
PREX 3G AS 2500 | 2907 | 2500020 | 3230 | 14 | Blu 4000.1 | ---- | PR * | TL - LONG | Maior P 400.1 | PAB | PR * | TL - LONG | Multicalor 400.1 | PAB | PR * | TL - LONG
PREX 3G AS 3000 | 3489 | 3000540 | 3876 | 12 | Blu 5000.1 | ---- | PR * | TL - LONG | Maior P 500.1 | PAB | PR * | TL - LONG | Multicalor 500.1 | ---- | PR * | TL - LONG
PREX 3G AS 3500 | 4070 | 3500200 | 4522 | 16 | Blu 6000.1 | ---- | PR * | TL - LONG | Maior P 600.1 | PAB | PR * | TL - LONG | Multicalor 600.1 | ---- | PR * | TL - LONG
PREX 3G AS 4000 | 4652 | 4000720 | 5168 | 13.5 | Blu 7000.1 | ---- | PR * | STD. | Maior P 700.1 | ---- | PR * | STD. | Multicalor 700.1 | ---- | PR * | STD.
PREX 3G AS 4500 | 5234 | 4501240 | 5815 | 20 | Blu 8000.1 | ---- | PR * | STD. | Maior P 800.1 | ---- | PR * | STD. | Multicalor 800.1 | ---- | PR * | STD.
PREX 3G AS 5000 | 5815 | 5000900 | 6461 | 14.5 | Blu 8000.1 | ---- | PR * | STD. | Maior P 800.1 | ---- | PR * | STD. | Multicalor 800.1 | ---- | PR * | STD.
PREX 3G AS 6000 | 6978 | 6001080 | 7753 | 20 | Blu 10000.1 | ---- | PR * | STD. | Maior P 1000.1 | ---- | PR * | STD. | Multicalor 1000.1 | ---- | PR * | STD.
PREX 3G AS 7200 | 8374 | 7201640 | 9304 | 19 | Blu 12000.1 | ---- | PR * | STD. | Maior P 1200.1 | ---- | PR * | STD. | Multicalor 1200.1 | ---- | PR * | STD.
PREX 3G AS 9000 | 10467 | 9001620 | 11630 | 24 | Blu 15000.1 | ---- | PR * | STD. | Maior P 1500.1 | ---- | PR * | STD. | Multicalor 1500.1 | ---- | PR * | STD.
PREX 3G AS 10000 | 11630 | 10001800 | 12922 | 28 | Blu 15000.1 | ---- | PR * | STD. | Maior P 1500.1 | ---- | PR * | STD. | Multicalor 1500.1 | ---- | PR * | STD.
PREX 3G AS 12000 | 14000 | 12040000 | 15600 | 34 | ------------- | ---- | PR * | STD. | ----------- | ---- | PR * | STD. | ----------- | ---- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli PREX 3G ASL - ASH
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
PREX 3G AS 1250 | 1454 | 1250440 | 1615 | 5.8 | Oilflam 200.1 | PAB | PR * | TL - LONG | Oilflam 200.1 | PAB | PR * | TL - LONG | Multiflam 200.1 | PAB | PR * | TL - LONG
PREX 3G AS 1500 | 1744 | 1499840 | 1937 | 7.1 | Oilflam 300.1 | ---- | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam 300.1 | PAB | PR * | TL - LONG
PREX 3G AS 1750 | 2034 | 1749240 | 2260 | 8.5 | Oilflam 300.1 | ---- | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam 300.1 | PAB | PR * | TL - LONG
PREX 3G AS 2000 | 2326 | 2000360 | 2584 | 10 | Oilflam 300.1 | ---- | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam 300.1 | PAB | PR * | TL - LONG
PREX 3G AS 2500 | 2907 | 2500020 | 3230 | 14 | Oilflam 400.1 | ---- | PR * | TL - LONG | Oilflam 400.1 | PAB | PR * | TL - LONG | Multiflam 400.1 | PAB | PR * | TL - LONG
PREX 3G AS 3000 | 3489 | 3000540 | 3876 | 12 | Oilflam 500.1 | ---- | PR * | TL - LONG | Oilflam 500.1 | PAB | PR * | TL - LONG | Multiflam 500.1 | ---- | PR * | TL - LONG
PREX 3G AS 3500 | 4070 | 3500200 | 4522 | 16 | Oilflam 600.1 | ---- | PR * | TL - LONG | Oilflam 600.1 | PAB | PR * | TL - LONG | Multiflam 600.1 | ---- | PR * | TL - LONG
PREX 3G AS 4000 | 4652 | 4000720 | 5168 | 13.5 | Oilflam 700.1 | ---- | PR * | STD. | Oilflam 700.1 | ---- | PR * | STD. | Multiflam 700.1 | ---- | PR * | STD.
PREX 3G AS 4500 | 5234 | 4501240 | 5815 | 20 | Oilflam 800.1 | ---- | PR * | STD. | Oilflam 800.1 | ---- | PR * | STD. | Multiflam 800.1 | ---- | PR * | STD.
PREX 3G AS 5000 | 5815 | 5000900 | 6461 | 14.5 | Oilflam 800.1 | ---- | PR * | STD. | Oilflam 800.1 | ---- | PR * | STD. | Multiflam 800.1 | ---- | PR * | STD.
PREX 3G AS 6000 | 6978 | 6001080 | 7753 | 20 | Oilflam 1000.1 | ---- | PR * | STD. | Oilflam 1000.1 | ---- | PR * | STD. | Multiflam 1000.1 | ---- | PR * | STD.
PREX 3G AS 7200 | 8374 | 7201640 | 9304 | 19 | Oilflam 1200.1 | ---- | PR * | STD. | Oilflam 1200.1 | ---- | PR * | STD. | Multiflam 1200.1 | ---- | PR * | STD.
PREX 3G AS 9000 | 10467 | 9001620 | 11630 | 24 | Oilflam 1500.1 | ---- | PR * | STD. | Oilflam 1500.1 | ---- | PR * | STD. | Multiflam 1500.1 | ---- | PR * | STD.
PREX 3G AS 10000 | 11630 | 10001800 | 12922 | 28 | Oilflam 1500.1 | ---- | PR * | STD. | Oilflam 1500.1 | ---- | PR * | STD. | Multiflam 1500.1 | ---- | PR * | STD.
PREX 3G AS 12000 | 14000 | 12040000 | 15600 | 34 | ----------- | ---- | PR * | STD. | ----------- | ---- | PR * | STD. | ----------- | ---- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## PREX ASH
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli PREX ASH
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
PREX ASH 140 | 163 | 140180 | 185 | 2 | MAX GAS 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | PR * | TL - LONG | DUAL 4 P | P | PAB | PR * | TL - LONG
PREX ASH 180 | 204 | 175440 | 231 | 2.3 | Blu 350 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
PREX ASH 240 | 268 | 230480 | 304 | 2.5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
PREX ASH 300 | 349 | 300140 | 396 | 2.8 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ---- | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
PREX ASH 360 | 407 | 350020 | 462 | 3.1 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ---- | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
PREX ASH 430 | 465 | 399900 | 528 | 3.3 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ---- | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
PREX ASH 510 | 582 | 500520 | 661 | 3.6 | Blu 1000 | P | PAB | PR * | TL - LONG | Maior P 60 | ---- | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
PREX ASH 600 | 698 | 600280 | 793 | 3.4 | Blu 1000 | P | PAB | PR * | TL - LONG | Maior P 80 | ---- | PAB | PR * | TL - LONG | Multicalor 100 | ---- | PAB | PR * | TL - LONG
PREX ASH 700 | 814 | 700040 | 924 | 3.9 | Blu 1400 | P | PAB | PR * | TL - LONG | Maior P 80 | ---- | PAB | PR * | TL - LONG | Multicalor 140 | ---- | PAB | PR * | TL - LONG
PREX ASH 800 | 930 | 799800 | 1056 | 4.5 | Blu 1400 | ---- | PAB | PR * | TL - LONG | Maior P 120 | ---- | PAB | PR * | TL - LONG | Multicalor 140 | ---- | PAB | PR * | TL - LONG
PREX ASH 1000 | 1163 | 1000180 | 1321 | 5.4 | Blu 1700.1 R | ---- | PAB | PR * | TL - LONG | Maior P 150.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 1250 | 1396 | 1200560 | 1586 | 6 | Blu 1700.1 | ---- | PAB | PR * | TL - LONG | Maior P 150.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 1500 | 1744 | 1499840 | 1981 | 6.8 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior P 200.1 | ---- | PAB | PR * | TL - LONG | Multicalor 200.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 1750 | 2035 | 1750100 | 2312 | 7.5 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior P 300.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 2000 | 2326 | 2000360 | 2642 | 8.2 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior P 300.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 2500 | 2907 | 2500020 | 3303 | 9 | Blu 4000.1 | ---- | ---- | PR * | TL - LONG | Maior P 400.1 | ---- | PAB | PR * | TL - LONG | Multicalor 400.1 | ---- | ---- | PR * | TL - LONG
PREX ASH 3000 | 3489 | 3000540 | 3963 | 10.2 | Blu 5000.1 | ---- | ---- | PR * | TL - LONG | Maior P 500.1 | ---- | PAB | PR * | TL - LONG | Multicalor 500.1 | ---- | ---- | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli PREX ASH
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
PREX ASH 140 | 163 | 140180 | 185 | 2 | Oilflam 20.1 | P | ---- | ---- | TL - LONG | Oilflam 20.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
PREX ASH 180 | 204 | 175440 | 231 | 2.3 | Oilflam 30.1 | P | ---- | ---- | TL - LONG | Oilflam 30.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
PREX ASH 240 | 268 | 230480 | 304 | 2.5 | Oilflam 30.1 | P | ---- | ---- | TL - LONG | Oilflam 30.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
PREX ASH 300 | 349 | 300140 | 396 | 2.8 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 50 | ---- | PAB | PR * | TL - LONG
PREX ASH 360 | 407 | 350020 | 462 | 3.1 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 50 | ---- | PAB | PR * | TL - LONG
PREX ASH 430 | 465 | 399900 | 528 | 3.3 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 70 | ---- | PAB | PR * | TL - LONG
PREX ASH 510 | 582 | 500520 | 661 | 3.6 | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Multiflam 70 | ---- | PAB | PR * | TL - LONG
PREX ASH 600 | 698 | 600280 | 793 | 3.4 | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
PREX ASH 700 | 814 | 700040 | 924 | 3.9 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
PREX ASH 800 | 930 | 799800 | 1056 | 4.5 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
PREX ASH 1000 | 1163 | 1000180 | 1321 | 5.4 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 1250 | 1396 | 1200560 | 1586 | 6 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 1500 | 1744 | 1499840 | 1981 | 6.8 | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Multiflam 200.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 1750 | 2035 | 1750100 | 2312 | 7.5 | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 2000 | 2326 | 2000360 | 2642 | 8.2 | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASH 2500 | 2907 | 2500020 | 3303 | 9 | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Multiflam 400.1 | ---- | ---- | PR * | TL - LONG
PREX ASH 3000 | 3489 | 3000540 | 3963 | 10.2 | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Multiflam 500.1 | ---- | ---- | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## PREX ASL
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli PREX ASL
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
PREX ASL 140 | 163 | 140180 | 185 | 2 | MAX GAS 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | PR * | TL - LONG | DUAL 4 P | P | PAB | PR * | TL - LONG
PREX ASL 175 | 204 | 175440 | 231 | 2.3 | Blu 350 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
PREX ASL 230 | 268 | 230480 | 304 | 2.5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
PREX ASL 300 | 349 | 300140 | 396 | 2.8 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ---- | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
PREX ASL 350 | 407 | 350020 | 462 | 3.1 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ---- | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
PREX ASL 400 | 465 | 399900 | 528 | 3.3 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ---- | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
PREX ASL 500 | 582 | 500520 | 661 | 3.6 | Blu 1000 | P | PAB | PR * | TL - LONG | Maior P 60 | ---- | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
PREX ASL 600 | 698 | 600280 | 793 | 3.4 | Blu 1000 | P | PAB | PR * | TL - LONG | Maior P 80 | ---- | PAB | PR * | TL - LONG | Multicalor 100 | ---- | PAB | PR * | TL - LONG
PREX ASL 700 | 814 | 700040 | 924 | 3.9 | Blu 1400 | P | PAB | PR * | TL - LONG | Maior P 80 | ---- | PAB | PR * | TL - LONG | Multicalor 140 | ---- | PAB | PR * | TL - LONG
PREX ASL 800 | 930 | 799800 | 1056 | 4.5 | Blu 1400 | ---- | PAB | PR * | TL - LONG | Maior P 120 | ---- | PAB | PR * | TL - LONG | Multicalor 140 | ---- | PAB | PR * | TL - LONG
PREX ASL 1000 | 1163 | 1000180 | 1321 | 5.4 | Blu 1700.1 R | ---- | PAB | PR * | TL - LONG | Maior P 150.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 1200 | 1396 | 1200560 | 1586 | 6 | Blu 1700.1 | ---- | PAB | PR * | TL - LONG | Maior P 150.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 1500 | 1744 | 1499840 | 1981 | 6.8 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior P 200.1 | ---- | PAB | PR * | TL - LONG | Multicalor 200.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 1750 | 2035 | 1750100 | 2312 | 7.5 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior P 300.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 2000 | 2326 | 2000360 | 2642 | 8.2 | Blu 3000.1 | ---- | ---- | PR * | TL - LONG | Maior P 300.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 2500 | 2907 | 2500020 | 3303 | 9 | Blu 4000.1 | ---- | ---- | PR * | TL - LONG | Maior P 400.1 | ---- | PAB | PR * | TL - LONG | Multicalor 400.1 | ---- | ---- | PR * | TL - LONG
PREX ASL 3000 | 3489 | 3000540 | 3963 | 10.2 | Blu 5000.1 | ---- | ---- | PR * | TL - LONG | Maior P 500.1 | ---- | PAB | PR * | TL - LONG | Multicalor 500.1 | ---- | ---- | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli PREX ASL
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
PREX ASL 140 | 163 | 140180 | 185 | 2 | Oilflam 20.1 | P | ---- | ---- | TL - LONG | Oilflam 20.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
PREX ASL 175 | 204 | 175440 | 231 | 2.3 | Oilflam 30.1 | P | ---- | ---- | TL - LONG | Oilflam 30.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
PREX ASL 230 | 268 | 230480 | 304 | 2.5 | Oilflam 30.1 | P | ---- | ---- | TL - LONG | Oilflam 30.1 | P | ---- | ---- | TL - LONG | ---------- | ------ | ------ | ------ | ------
PREX ASL 300 | 349 | 300140 | 396 | 2.8 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 50 | ---- | PAB | PR * | TL - LONG
PREX ASL 350 | 407 | 350020 | 462 | 3.1 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 50 | ---- | PAB | PR * | TL - LONG
PREX ASL 400 | 465 | 399900 | 528 | 3.3 | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Oilflam 50.1 | ---- | PAB | PR * | TL - LONG | Multiflam 70 | ---- | PAB | PR * | TL - LONG
PREX ASL 500 | 582 | 500520 | 661 | 3.6 | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Multiflam 70 | ---- | PAB | PR * | TL - LONG
PREX ASL 600 | 698 | 600280 | 793 | 3.4 | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Oilflam 80.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
PREX ASL 700 | 814 | 700040 | 924 | 3.9 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
PREX ASL 800 | 930 | 799800 | 1056 | 4.5 | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Oilflam 120.1 | ---- | PAB | PR * | TL - LONG | Multiflam 120 | ---- | PAB | PR * | TL - LONG
PREX ASL 1000 | 1163 | 1000180 | 1321 | 5.4 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 1200 | 1396 | 1200560 | 1586 | 6 | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Oilflam 170.1 | ---- | PAB | PR * | TL - LONG | Multiflam 170.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 1500 | 1744 | 1499840 | 1981 | 6.8 | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Oilflam 200.1 | ---- | PAB | PR * | TL - LONG | Multiflam 200.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 1750 | 2035 | 1750100 | 2312 | 7.5 | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 2000 | 2326 | 2000360 | 2642 | 8.2 | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Oilflam 300.1 | ---- | PAB | PR * | TL - LONG | Multiflam 300.1 | ---- | PAB | PR * | TL - LONG
PREX ASL 2500 | 2907 | 2500020 | 3303 | 9 | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Oilflam 400.1 | ---- | PAB | PR * | TL - LONG | Multiflam 400.1 | ---- | ---- | PR * | TL - LONG
PREX ASL 3000 | 3489 | 3000540 | 3963 | 10.2 | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Oilflam 500.1 | ---- | PAB | PR * | TL - LONG | Multiflam 500.1 | ---- | ---- | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VAPOPREX 3G
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli VAPOPREX 3G
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | LIGHT OIL BURNER
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
VAPOPREX 3G 1250 | 1454 | 1250440 | 1615 | 5.8 | Blu 2000.1 | PAB | PR * | TL - LONG | Maior P 200.1 | PAB | PR * | TL - LONG | Multicalor 200.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 1500 | 1744 | 1499840 | 1937 | 7.1 | Blu 2000.1 | PAB | PR * | TL - LONG | Maior P 200.1 | PAB | PR * | TL - LONG | Multicalor 200.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 1750 | 2034 | 1749240 | 2260 | 8.5 | Blu 3000.1 | ----- | PR * | TL - LONG | Maior P 300.1 | PAB | PR * | TL - LONG | Multicalor 300.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 2000 | 2326 | 2000360 | 2584 | 10 | Blu 3000.1 | ----- | PR * | TL - LONG | Maior P 300.1 | PAB | PR * | TL - LONG | Multicalor 300.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 2500 | 2907 | 2500020 | 3230 | 14 | Blu 5000.1 | ----- | PR * | TL - LONG | Maior P 500.1 | PAB | PR * | TL - LONG | Multicalor 500.1 | ----- | PR * | TL - LONG
VAPOPREX 3G 3000 | 3489 | 3000540 | 3876 | 12 | Blu 5000.1 | ----- | PR * | TL - LONG | Maior P 500.1 | PAB | PR * | TL - LONG | Multicalor 500.1 | ----- | PR * | TL - LONG
VAPOPREX 3G 3500 | 4070 | 3500200 | 4522 | 16 | Blu 6000.1 | ----- | PR * | TL - LONG | Maior P 600.1 | PAB | PR * | TL - LONG | Multicalor 600.1 | ----- | PR * | TL - LONG
VAPOPREX 3G 4000 | 4652 | 4000720 | 5168 | 13.5 | Blu 7000.1 | ----- | PR * | STD. | Maior P 700.1 | ----- | PR * | STD. | Multicalor 700.1 | ----- | PR * | STD.
VAPOPREX 3G 4500 | 5234 | 4501240 | 5815 | 20 | Blu 8000.1 | ----- | PR * | STD. | Maior P 800.1 | ----- | PR * | STD. | Multicalor 800.1 | ----- | PR * | STD.
VAPOPREX 3G 5000 | 5815 | 5000900 | 6461 | 14.5 | Blu 8000.1 | ----- | PR * | STD. | Maior P 800.1 | ----- | PR * | STD. | Multicalor 800.1 | ----- | PR * | STD.
VAPOPREX 3G 6000 | 6978 | 6001080 | 7753 | 20 | Blu 10000.1 | ----- | PR * | STD. | Maior P 1000.1 | ----- | PR * | STD. | Multicalor 1000.1 | ----- | PR * | STD.
VAPOPREX 3G 7200 | 8374 | 7201640 | 9304 | 19 | Blu 12000.1 | ----- | PR * | STD. | Maior P 1200.1 | ----- | PR * | STD. | Multicalor 1200.1 | ----- | PR * | STD.
VAPOPREX 3G 9000 | 10467 | 9001620 | 11630 | 24 | Blu 15000.1 | ----- | PR * | STD. | Maior P 1500.1 | ----- | PR * | STD. | Multicalor 1500.1 | ----- | PR * | STD.
VAPOPREX 3G 10400 | 12095 | 10401700 | 13468 | 28 | Blu 15000.1 | ----- | PR * | STD. | Maior P 1500.1 | ----- | PR * | STD. | Multicalor 1500.1 | ----- | PR * | STD.
VAPOPREX 3G 12000 | 14000 | 12040000 | 15600 | 34 | ------------- | ----- | PR * | STD. | ----------- | ----- | PR * | STD. | ----------- | ----- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli VAPOPREX 3G
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
VAPOPREX 3G 1250 | 1454 | 1250440 | 1615 | 5.8 | Oilflam 200.1 | PAB | PR * | TL - LONG | Oilflam 200.1 | PAB | PR * | TL - LONG | Multiflam 200.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 1500 | 1744 | 1499840 | 1937 | 7.1 | Oilflam 200.1 | PAB | PR * | TL - LONG | Oilflam 200.1 | PAB | PR * | TL - LONG | Multiflam 200.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 1750 | 2034 | 1749240 | 2260 | 8.5 | Oilflam 300.1 | ----- | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam 300.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 2000 | 2326 | 2000360 | 2584 | 10 | Oilflam 300.1 | ----- | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam 300.1 | PAB | PR * | TL - LONG
VAPOPREX 3G 2500 | 2907 | 2500020 | 3230 | 14 | Oilflam 500.1 | ----- | PR * | TL - LONG | Oilflam 500.1 | PAB | PR * | TL - LONG | Multiflam 500.1 | ----- | PR * | TL - LONG
VAPOPREX 3G 3000 | 3489 | 3000540 | 3876 | 12 | Oilflam 500.1 | ----- | PR * | TL - LONG | Oilflam 500.1 | PAB | PR * | TL - LONG | Multiflam 500.1 | ----- | PR * | TL - LONG
VAPOPREX 3G 3500 | 4070 | 3500200 | 4522 | 16 | Oilflam 600.1 | ----- | PR * | TL - LONG | Oilflam 600.1 | PAB | PR * | TL - LONG | Multiflam 600.1 | ----- | PR * | TL - LONG
VAPOPREX 3G 4000 | 4652 | 4000720 | 5168 | 13.5 | Oilflam 700.1 | ----- | PR * | STD. | Oilflam 700.1 | ----- | PR * | STD. | Multiflam 700.1 | ----- | PR * | STD.
VAPOPREX 3G 4500 | 5234 | 4501240 | 5815 | 20 | Oilflam 800.1 | ----- | PR * | STD. | Oilflam 800.1 | ----- | PR * | STD. | Multiflam 800.1 | ----- | PR * | STD.
VAPOPREX 3G 5000 | 5815 | 5000900 | 6461 | 14.5 | Oilflam 800.1 | ----- | PR * | STD. | Oilflam 800.1 | ----- | PR * | STD. | Multiflam 800.1 | ----- | PR * | STD.
VAPOPREX 3G 6000 | 6978 | 6001080 | 7753 | 20 | Oilflam 1000.1 | ----- | PR * | STD. | Oilflam 1000.1 | ----- | PR * | STD. | Multiflam 1000.1 | ----- | PR * | STD.
VAPOPREX 3G 7200 | 8374 | 7201640 | 9304 | 19 | Oilflam 1200.1 | ----- | PR * | STD. | Oilflam 1200.1 | ----- | PR * | STD. | Multiflam 1200.1 | ----- | PR * | STD.
VAPOPREX 3G 9000 | 10467 | 9001620 | 11630 | 24 | Oilflam 1500.1 | ----- | PR * | STD. | Oilflam 1500.1 | ----- | PR * | STD. | Multiflam 1500.1 | ----- | PR * | STD.
VAPOPREX 3G 10400 | 12095 | 10401700 | 13468 | 28 | Oilflam 1500.1 | ----- | PR * | STD. | Oilflam 1500.1 | ----- | PR * | STD. | Multiflam 1500.1 | ----- | PR * | STD.
VAPOPREX 3G 12000 | 14000 | 12040000 | 15600 | 34 | ----------- | ----- | PR * | STD. | ----------- | ----- | PR * | STD. | ----------- | ----- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VAPOPREX LVP
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli VAPOPREX LVP
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VAPOPREX LVP 160 | 112 | 96320 | 124 | 2 | MAX GAS 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | PR * | TL - LONG | DUAL 4 P | P | PAB | PR * | TL - LONG
VAPOPREX LVP 250 | 174 | 149640 | 193 | 3.8 | MAX GAS 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
VAPOPREX LVP 300 | 209 | 179740 | 232 | 5.5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
VAPOPREX LVP 400 | 279 | 239940 | 310 | 3.5 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ----- | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
VAPOPREX LVP 500 | 349 | 300140 | 387 | 4.5 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor 45 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 600 | 419 | 360340 | 465 | 6.8 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor 45 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 800 | 558 | 479880 | 620 | 4.6 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 80 | ----- | PAB | PR * | TL - LONG | Multicalor 70 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 1000 | 698 | 600280 | 775 | 7.2 | Blu 1400 | ----- | PAB | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor 100 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 1500 | 1047 | 900420 | 1163 | 5.1 | Blu 1700.1 R | ----- | PAB | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor 170.1 | ----- | PAB | PR * | TC - SHORT
VAPOPREX LVP 2000 | 1389 | 1194540 | 1543 | 7.2 | Blu 1700.1 | ----- | PAB | PR * | TC - SHORT | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor 170.1 | ----- | PAB | PR * | TC - SHORT
VAPOPREX LVP 2500 | 1745 | 1500700 | 1938 | 6.2 | Blu 2000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 200.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 200.1 | ----- | PAB | PR * | TC - SHORT
VAPOPREX LVP 3000 | 2086 | 1793960 | 2317 | 7.8 | Blu 3000.1 | ----- | PAB | PR * | TL - LONG | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor 300.1 | ----- | PAB | PR * | TL - LONG
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VAPOPREX LVP 160 | 112 | 96320 | 124 | 2 | Oilflam 15.1 | P | PAB | PR * | TL - LONG | Oilflam 15.1 | P | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX LVP 250 | 174 | 149640 | 193 | 3.8 | Oilflam 20.1 | P | PAB | PR * | TL - LONG | Oilflam 20.1 | P | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX LVP 300 | 209 | 179740 | 232 | 5.5 | Oilflam 30.1 | P | PAB | PR * | TL - LONG | Oilflam 30.1 | P | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX LVP 400 | 279 | 239940 | 310 | 3.5 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX LVP 500 | 349 | 300140 | 387 | 4.5 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 600 | 419 | 360340 | 465 | 6.8 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 800 | 558 | 479880 | 620 | 4.6 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 70 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 1000 | 698 | 600280 | 775 | 7.2 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 1500 | 1047 | 900420 | 1163 | 5.1 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 2000 | 1389 | 1194540 | 1543 | 7.2 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 2500 | 1745 | 1500700 | 1938 | 6.2 | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Multiflam 200.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX LVP 3000 | 2086 | 1793960 | 2317 | 7.8 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VAPOPREX HPV
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli VAPOPREX HVP
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VAPOPREX HVP 160 | 105 | 90300 | 116 | 2 | MAX GAS 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | PR * | TL - LONG | DUAL 4 P | P | PAB | PR * | TL - LONG
VAPOPREX HVP 250 | 174 | 149640 | 193 | 3.8 | MAX GAS 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
VAPOPREX HVP 300 | 209 | 179740 | 232 | 5.5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
VAPOPREX HVP 400 | 279 | 239940 | 310 | 3.5 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ----- | PAB | PR * | TL - LONG | DUAL 5 P | P | PAB | PR * | TL - LONG
VAPOPREX HVP 500 | 349 | 300140 | 387 | 4.5 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor 45 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 600 | 419 | 360340 | 465 | 6.8 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor 45 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 800 | 558 | 479880 | 620 | 4.6 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 80 | ----- | PAB | PR * | TL - LONG | Multicalor 70 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 1000 | 698 | 600280 | 775 | 7.2 | Blu 1400 | ----- | PAB | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor 100 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 1500 | 1047 | 900420 | 1163 | 5.1 | Blu 1700.1 R | ----- | PAB | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor 170.1 | ----- | PAB | PR * | TC - SHORT
VAPOPREX HVP 2000 | 1389 | 1194540 | 1543 | 7.2 | Blu 1700.1 | ----- | PAB | PR * | TC - SHORT | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor 170.1 | ----- | PAB | PR * | TC - SHORT
VAPOPREX HVP 2500 | 1745 | 1500700 | 1938 | 6.2 | Blu 2000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 200.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 200.1 | ----- | PAB | PR * | TC - SHORT
VAPOPREX HVP 3000 | 2086 | 1793960 | 2317 | 7.8 | Blu 3000.1 | ----- | PAB | PR * | TL - LONG | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor 300.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 4000 | 2791 | 2400260 | 3101 | 8 | Blu 4000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 400.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 400.1 | ----- | PAB | PR * | TC - SHORT
VAPOPREX HVP 5000 | 2482 | 2134520 | 3868 | 10.5 | Blu 5000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 500.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 500.1 | ----- | PAB | PR * | TC - SHORT
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VAPOPREX HVP 160 | 105 | 90300 | 116 | 2 | Oilflam 15.1 | P | PAB | PR * | TL - LONG | Oilflam 15.1 | P | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX HVP 250 | 174 | 149640 | 193 | 3.8 | Oilflam 20.1 | P | PAB | PR * | TL - LONG | Oilflam 20.1 | P | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX HVP 300 | 209 | 179740 | 232 | 5.5 | Oilflam 30.1 | P | PAB | PR * | TL - LONG | Oilflam 30.1 | P | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX HVP 400 | 279 | 239940 | 310 | 3.5 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | ---------- | ------ | ------ | ------ | ------
VAPOPREX HVP 500 | 349 | 300140 | 387 | 4.5 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 600 | 419 | 360340 | 465 | 6.8 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 800 | 558 | 479880 | 620 | 4.6 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 70 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 1000 | 698 | 600280 | 775 | 7.2 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 1500 | 1047 | 900420 | 1163 | 5.1 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 2000 | 1389 | 1194540 | 1543 | 7.2 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 2500 | 1745 | 1500700 | 1938 | 6.2 | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Multiflam 200.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 3000 | 2086 | 1793960 | 2317 | 7.8 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 4000 | 2791 | 2400260 | 3101 | 8 | Oilflam 400.1 | ----- | PAB | PR * | TL - LONG | Oilflam 400.1 | ----- | PAB | PR * | TL - LONG | Multiflam 400.1 | ----- | PAB | PR * | TL - LONG
VAPOPREX HVP 5000 | 2482 | 2134520 | 3868 | 10.5 | Oilflam 500.1 | ----- | PAB | PR * | TL - LONG | Oilflam 500.1 | ----- | PAB | PR * | TL - LONG | Multiflam 500.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## EVA
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli EVA
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
EVA 100 | 117 | 100620 | 136.0465 | 1.5 | MAX GAS 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | PR * | TC - SHORT | DUAL 4 P | P | ----- | ----- | TC - SHORT
EVA 200 | 233 | 200380 | 270.9302 | 2 | Blu 350 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ----- | TC - SHORT | DUAL 5 P | P | ----- | ----- | TC - SHORT
EVA 320 | 372 | 319920 | 432.5581 | 2.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ----- | PAB | PR * | TC - SHORT | Multicalor 45 | ----- | PAB | PR * | TC - SHORT
EVA 400 | 465 | 399900 | 540.6977 | 3 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ----- | PAB | PR * | TC - SHORT | Multicalor 70 | ----- | PAB | PR * | TC - SHORT
EVA 500 | 581 | 499660 | 675.5814 | 3.2 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ----- | PAB | PR * | TC - SHORT | Multicalor 70 | ----- | PAB | PR * | TC - SHORT
EVA 640 | 745 | 640700 | 866.2791 | 3.4 | Blu 1000 | P | PAB | PR * | TC - SHORT | Maior P 80 | ----- | PAB | PR * | TC - SHORT | Multicalor 100 | ----- | PAB | PR * | TC - SHORT
EVA 800 | 930 | 799800 | 1081.3953 | 3.5 | Blu 1400 | ----- | PAB | PR * | TC - SHORT | Maior P 120 | ----- | PAB | PR * | TC - SHORT | Multicalor 140 | ----- | PAB | PR * | TC - SHORT
EVA 1000 | 1163 | 1000180 | 1352.3256 | 3.8 | Blu 1700.1 R | ----- | PAB | PR * | TC - SHORT | Maior P 150.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 170.1 | ----- | PAB | PR * | TC - SHORT
EVA 1300 | 1512 | 1300320 | 1758.1395 | 4 | Blu 2000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 200.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 200.1 | ----- | PAB | PR * | TC - SHORT
EVA 1600 | 1862 | 1601320 | 2165.1163 | 4.2 | Blu 3000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 200.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 300.1 | ----- | PAB | PR * | TC - SHORT
EVA 2000 | 2327 | 2001220 | 2705.814 | 4.5 | Blu 3000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 300.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 300.1 | ----- | PAB | PR * | TC - SHORT
EVA 2500 | 2909 | 2501740 | 3382.5581 | 4.5 | Blu 4000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 400.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 400.1 | ----- | PAB | PR * | TC - SHORT
EVA 3000 | 3491 | 3002260 | 4059.3023 | 5 | Blu 5000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 500.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 500.1 | ----- | PAB | PR * | TC - SHORT
EVA 4000 | 4652 | 4000720 | 5409.3023 | 6 | Blu 6000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 600.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 600.1 | ----- | PAB | PR * | TC - SHORT
EVA 5000 | 5814 | 5000040 | 6760.4651 | 7 | Blu 7000.1 | ----- | PAB | PR * | STD. | Maior P 700.1 | ----- | PAB | PR * | STD. | Multicalor 700.1 | ----- | PAB | PR * | STD.
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
EVA 100 | 117 | 100620 | 136.0465 | 1.5 | Oilflam 15.1 | P | ----- | ----- | TC - SHORT | Oilflam 15.1 | P | ----- | ----- | TC - SHORT | ---------- | ------ | ------ | ------ | ------
EVA 200 | 233 | 200380 | 270.9302 | 2 | Oilflam 30.1 | P | ----- | ----- | TC - SHORT | Oilflam 30.1 | P | ----- | ----- | TC - SHORT | ---------- | ------ | ------ | ------ | ------
EVA 320 | 372 | 319920 | 432.5581 | 2.5 | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 50 | ----- | PAB | PR * | TC - SHORT
EVA 400 | 465 | 399900 | 540.6977 | 3 | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 70 | ----- | PAB | PR * | TC - SHORT
EVA 500 | 581 | 499660 | 675.5814 | 3.2 | Oilflam 80.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 80.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 70 | ----- | PAB | PR * | TC - SHORT
EVA 640 | 745 | 640700 | 866.2791 | 3.4 | Oilflam 80.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 120.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 120 | ----- | PAB | PR * | TC - SHORT
EVA 800 | 930 | 799800 | 1081.3953 | 3.5 | Oilflam 120.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 120.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 120 | ----- | PAB | PR * | TC - SHORT
EVA 1000 | 1163 | 1000180 | 1352.3256 | 3.8 | Oilflam 170.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 170.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 170.1 | ----- | PAB | PR * | TC - SHORT
EVA 1300 | 1512 | 1300320 | 1758.1395 | 4 | Oilflam 200.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 200.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 200.1 | ----- | PAB | PR * | TC - SHORT
EVA 1600 | 1862 | 1601320 | 2165.1163 | 4.2 | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 300.1 | ----- | PAB | PR * | TC - SHORT
EVA 2000 | 2327 | 2001220 | 2705.814 | 4.5 | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 300.1 | ----- | PAB | PR * | TC - SHORT
EVA 2500 | 2909 | 2501740 | 3382.5581 | 4.5 | Oilflam 400.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 400.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 400.1 | ----- | PAB | PR * | TC - SHORT
EVA 3000 | 3491 | 3002260 | 4059.3023 | 5 | Oilflam 500.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 500.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 500.1 | ----- | PAB | PR * | TC - SHORT
EVA 4000 | 4652 | 4000720 | 5409.3023 | 6 | Oilflam 600.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 600.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 600.1 | ----- | PAB | PR * | TC - SHORT
EVA 5000 | 5814 | 5000040 | 6760.4651 | 7 | Oilflam 700.1 | ----- | PAB | PR * | STD. | Oilflam 700.1 | ----- | PAB | PR * | STD. | Multiflam 700.1 | ----- | PAB | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ELICOIL NO
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: Ferroli ELICOIL NO
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
ELICOIL NO 100 | 116 | 99760 | 134 | 1.5 | MAX GAS 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | PR * | TC - SHORT | DUAL 4 P | P | ----- | ----- | TC - SHORT
ELICOIL NO 200 | 232 | 199520 | 267 | 2 | Blu 350 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ----- | TC - SHORT | DUAL 5 P | P | ----- | ----- | TC - SHORT
ELICOIL NO 320 | 372 | 319920 | 427 | 2.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ----- | PAB | PR * | TC - SHORT | Multicalor 45 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 400 | 465 | 399900 | 534 | 3 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ----- | PAB | PR * | TC - SHORT | Multicalor 70 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 500 | 581 | 499660 | 668 | 3.2 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ----- | PAB | PR * | TC - SHORT | Multicalor 70 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 640 | 744 | 639840 | 855 | 3.4 | Blu 1000 | P | PAB | PR * | TC - SHORT | Maior P 80 | ----- | PAB | PR * | TC - SHORT | Multicalor 100 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 800 | 930 | 799800 | 1069 | 3.5 | Blu 1400 | ----- | PAB | PR * | TC - SHORT | Maior P 120 | ----- | PAB | PR * | TC - SHORT | Multicalor 140 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 1000 | 1163 | 1000180 | 1337 | 3.8 | Blu 1700.1 R | ----- | PAB | PR * | TC - SHORT | Maior P 150.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 170.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 1300 | 1512 | 1300320 | 1738 | 4 | Blu 2000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 200.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 200.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 1600 | 1861 | 1600460 | 2139 | 4.2 | Blu 3000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 200.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 300.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 2000 | 2326 | 2000360 | 2673 | 4.5 | Blu 3000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 300.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 300.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 2500 | 2907 | 2500020 | 3342 | 4.5 | Blu 4000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 400.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 400.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 3000 | 3489 | 3000540 | 4010 | 5 | Blu 5000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 500.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 500.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 4000 | 4652 | 4000720 | 5347 | 6 | Blu 6000.1 | ----- | PAB | PR * | TC - SHORT | Maior P 600.1 | ----- | PAB | PR * | TC - SHORT | Multicalor 600.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 5000 | 5815 | 5000900 | 6684 | 7 | Blu 7000.1 | ----- | PAB | PR * | STD. | Maior P 700.1 | ----- | PAB | PR * | STD. | Multicalor 700.1 | ----- | PAB | PR * | STD.
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
ELICOIL NO 100 | 116 | 99760 | 134 | 1.5 | Oilflam 15.1 | P | ----- | ----- | TC - SHORT | Oilflam 15.1 | P | ----- | ----- | TC - SHORT | ---------- | ------ | ------ | ------ | ------
ELICOIL NO 200 | 232 | 199520 | 267 | 2 | Oilflam 30.1 | P | ----- | ----- | TC - SHORT | Oilflam 30.1 | P | ----- | ----- | TC - SHORT | ---------- | ------ | ------ | ------ | ------
ELICOIL NO 320 | 372 | 319920 | 427 | 2.5 | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 50 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 400 | 465 | 399900 | 534 | 3 | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 50.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 70 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 500 | 581 | 499660 | 668 | 3.2 | Oilflam 80.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 80.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 70 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 640 | 744 | 639840 | 855 | 3.4 | Oilflam 80.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 120.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 120 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 800 | 930 | 799800 | 1069 | 3.5 | Oilflam 120.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 120.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 120 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 1000 | 1163 | 1000180 | 1337 | 3.8 | Oilflam 170.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 170.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 170.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 1300 | 1512 | 1300320 | 1738 | 4 | Oilflam 200.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 200.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 200.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 1600 | 1861 | 1600460 | 2139 | 4.2 | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 300.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 2000 | 2326 | 2000360 | 2673 | 4.5 | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 300.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 2500 | 2907 | 2500020 | 3342 | 4.5 | Oilflam 400.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 400.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 400.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 3000 | 3489 | 3000540 | 4010 | 5 | Oilflam 500.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 500.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 500.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 4000 | 4652 | 4000720 | 5347 | 6 | Oilflam 600.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 600.1 | ----- | PAB | PR * | TC - SHORT | Multiflam 600.1 | ----- | PAB | PR * | TC - SHORT
ELICOIL NO 5000 | 5815 | 5000900 | 6684 | 7 | Oilflam 700.1 | ----- | PAB | PR * | STD. | Oilflam 700.1 | ----- | PAB | PR * | STD. | Multiflam 700.1 | ----- | PAB | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE