## BLUNOx
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI - BLUNOx
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER
[5 empty] | MODEL | ON OFF | HI LOW | BLAST TUBE | MODEL | ON OFF | HI LOW | BLAST TUBE
BLUNOx 19 | 22 | 18920 | 24 | 0.2 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG
BLUNOx 27 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG
BLUNOx 34 | 40 | 34400 | 43.8 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 4 Low NOx | OK | ------ | TL - LONG
BLUNOx 43 | 50 | 43000 | 54.8 | 0.4 | MAX GAS 70 | P | PAB | TL - LONG | Max 4 Low NOx | OK | ------ | TL - LONG
BLUNOx 60 | 70 | 60200 | 76.5 | 0.4 | MAX GAS 105 | P | PAB | TC - SHORT | Max 8 Low NOx | OK | ------ | TC - SHORT
BLUNOx B 19/150 | 22 | 18920 | 24 | 0.25 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG
BLUNOx B 27/150 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG
BLUNOx B 27/200 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 4 Low NOx | OK | ------ | TL - LONG
BLUNOx B 27/250 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 4 Low NOx | OK | ------ | TL - LONG
BLUNOx B 34/150 | 40 | 34400 | 43.8 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 4 Low NOx | OK | ------ | TL - LONG
BLUNOx B 34/200 | 40 | 34400 | 43.8 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 4 Low NOx | OK | ------ | TL - LONG
BLUNOx B 34/250 | 40 | 34400 | 43.8 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 4 Low NOx | OK | ------ | TL - LONG
BLUNOx B 43/150 | 50 | 43000 | 54.8 | 0.4 | MAX GAS 70 | P | PAB | TL - LONG | Max 8 Low NOx | OK | ------ | TL - LONG
BLUNOx B 43/200 | 50 | 43000 | 54.8 | 0.4 | MAX GAS 70 | P | PAB | TL - LONG | Max 8 Low NOx | OK | ------ | TL - LONG
BLUNOx B 43/250 | 50 | 43000 | 54.8 | 0.4 | MAX GAS 70 | P | PAB | TL - LONG | Max 8 Low NOx | OK | ------ | TL - LONG
BLUNOx B 60/150 | 70 | 60200 | 76.5 | 0.4 | MAX GAS 105 | P | PAB | TC - SHORT | Max 8 Low NOx | OK | ------ | TC - SHORT
BLUNOx B 60/200 | 70 | 60200 | 76.5 | 0.4 | MAX GAS 105 | P | PAB | TC - SHORT | Max 8 Low NOx | OK | ------ | TC - SHORT
BLUNOx B 60/250 | 70 | 60200 | 76.5 | 0.4 | MAX GAS 105 | P | PAB | TC - SHORT | Max 8 Low NOx | OK | ------ | TC - SHORT
BLUNOx BT 27 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG
BLUNOx B BT 27/150 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG
BLUNOx B BT 27/200 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG
BLUNOx B BT 27/250 | 31.4 | 27004 | 34.3 | 0.3 | MAX GAS 40 | P | ------ | TL - LONG | Max 1 Low NOx | OK | ------ | TL - LONG

## GREENOx
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI - GREENOx
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | DUAL FUEL BURNER
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
GREENOx 12 | 120 | 103200 | 129 | 1.1 | Max Gas 170 | P | PAB | PR * | TL - LONG | Dual 4 P | P | ---- | ---- | TL - LONG
GREENOx 15 | 150 | 129000 | 162 | 2 | Max Gas 170 | P | PAB | PR * | TL - LONG | Dual 4 P | P | ---- | ---- | TL - LONG
GREENOx 20 | 200 | 172000 | 214 | 2.1 | Blu 350 | P | PAB | PR * | TC - SHORT | Dual 5 P | P | ---- | ---- | TC - SHORT
GREENOx 25 | 250 | 215000 | 269 | 2 | Blu 350 | P | PAB | PR * | TC - SHORT | Dual 5 P | P | ---- | ---- | TC - SHORT
GREENOx 30 | 300 | 258000 | 324 | 3.5 | Blu 500 | P | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
GREENOx 35 | 250 | 215000 | 376 | 3.1 | Blu 500 | P | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
GREENOx 40 | 400 | 344000 | 432 | 3.1 | Blu 500 | P | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
GREENOx 47 | 470 | 404200 | 506 | 3.7 | Blu 700 | P | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
GREENOx 60 | 600 | 516000 | 649 | 3.9 | Blu 1000 | ---- | PAB | PR * | TL - LONG | Multicalor 100 | ---- | PAB | PR * | TL - LONG
GREENOx 70 | 700 | 602000 | 757 | 4.5 | Blu 1000 | ---- | PAB | PR * | TL - LONG | Multicalor 120 | ---- | PAB | PR * | TL - LONG
GREENOx 80 | 800 | 688000 | 870 | 2.2 | Blu 1000 | ---- | PAB | PR * | TL - LONG | Multicalor 120 | ---- | PAB | PR * | TL - LONG
GREENOx 90 | 900 | 774000 | 978 | 2.8 | Blu 1400 | ---- | PAB | PR * | TC - SHORT | Multicalor 120 | ---- | PAB | PR * | TC - SHORT
GREENOx 100 | 1000 | 860000 | 1087 | 2.1 | Blu 1400 | ---- | PAB | PR * | TC - SHORT | Multicalor 120 | ---- | PAB | PR * | TC - SHORT
GREENOx 120 | 1200 | 1032000 | 1304 | 3.2 | Blu 1700.1 R | ---- | PAB | PR * | TL - LONG | Multicalor 150.1 | ---- | PAB | PR * | TL - LONG
GREENOx 140 | 1400 | 1204000 | 1522 | 4.4 | Blu 1700.1 | ---- | PAB | PR * | TL - LONG | Multicalor 150.1 | ---- | PAB | PR * | TL - LONG
GREENOx 170 | 1700 | 1462000 | 1848 | 5 | Blu 2000.1 | ---- | PAB | PR * | TL - LONG | Multicalor 200.1 | ---- | PAB | PR * | TL - LONG
GREENOx 200 | 2000 | 1720000 | 2174 | 7 | Blu 3000.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
GREENOx 230 | 2300 | 1978000 | 2500 | 7.5 | Blu 3000.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## GREENOx BT
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI - GREENOx BT
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | DUAL FUEL BURNER
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
GREENOx BT 10 | 100 | 86000 | 107 | 1.4 | Max Gas 120 | P | PAB | PR * | TL - LONG | Dual 4 P | P | ---- | ---- | TL - LONG
GREENOx BT 12 | 120 | 103200 | 129 | 2.2 | Max Gas 170 | P | PAB | PR * | TL - LONG | Dual 4 P | P | ---- | ---- | TL - LONG
GREENOx BT 15 | 150 | 129000 | 162 | 2.2 | Max Gas 250 | P | PAB | PR * | TL - LONG | Dual 4 P | P | ---- | ---- | TL - LONG
GREENOx BT 20 | 200 | 172000 | 214 | 2 | Max Gas 250 | P | PAB | PR * | TL - LONG | Dual 5 P | P | ---- | ---- | TL - LONG
GREENOx BT 25 | 250 | 215000 | 269 | 2.8 | Blu 350 | P | PAB | PR * | TC - SHORT | Dual 5 P | P | ---- | ---- | TC - SHORT
GREENOx BT 30 | 300 | 258000 | 324 | 3.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Multicalor 45 | ---- | PAB | PR * | TC - SHORT
GREENOx BT 35 | 250 | 215000 | 376 | 3.6 | Blu 500 | P | PAB | PR * | TL - LONG | Multicalor 45 | ---- | PAB | PR * | TL - LONG
GREENOx BT 40 | 400 | 344000 | 432 | 4.5 | Blu 500 | P | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
GREENOx BT 47 | 470 | 404200 | 506 | 4 | Blu 700 | P | PAB | PR * | TL - LONG | Multicalor 70 | ---- | PAB | PR * | TL - LONG
GREENOx BT 60 | 600 | 516000 | 649 | 5 | Blu 1000 | ---- | PAB | PR * | TL - LONG | Multicalor 100 | ---- | PAB | PR * | TL - LONG
GREENOx BT 70 | 700 | 602000 | 757 | 2.7 | Blu 1000 | ---- | PAB | PR * | TL - LONG | Multicalor 120 | ---- | PAB | PR * | TL - LONG
GREENOx BT 90 | 900 | 774000 | 978 | 3.5 | Blu 1400 | ---- | PAB | PR * | TC - SHORT | Multicalor 120 | ---- | PAB | PR * | TC - SHORT
GREENOx BT 100 | 1000 | 860000 | 1087 | 5.1 | Blu 1700.1 R | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
GREENOx BT 120 | 1200 | 1032000 | 1304 | 5.4 | Blu 1700.1 R | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
GREENOx BT 140 | 1400 | 1204000 | 1522 | 8 | Blu 1700.1 | ---- | PAB | PR * | TL - LONG | Multicalor 170.1 | ---- | PAB | PR * | TL - LONG
GREENOx BT 170 | 1700 | 1462000 | 1848 | 8.5 | Blu 3000.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
GREENOx BT 200 | 2000 | 1720000 | 2174 | 7 | Blu 3000.1 | ---- | PAB | PR * | TL - LONG | Multicalor 300.1 | ---- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ICI REX
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI - REX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
REX 7 | 70 | 60200 | 76 | 0.8 | Max Gas 105 | P | PAB | ------ | TL - LONG | Max P 8 | P | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TC - SHORT
REX 8 | 80 | 68800 | 87 | 1 | Max Gas 105 | P | PAB | ------ | TL - LONG | Max P 8 | P | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TC - SHORT
REX 9 | 90 | 77400 | 98 | 0.8 | Max Gas 105 | P | PAB | ------ | TL - LONG | Max P 8 | P | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TC - SHORT
REX 10 | 100 | 86000 | 109 | 1 | Max Gas 120 | P | PAB | ------ | TL - LONG | Max P 12 | P | ------ | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
REX 12 | 120 | 103200 | 131 | 1.1 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
REX 15 | 150 | 129000 | 163 | 1.2 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
REX 20 | 200 | 172000 | 218 | 1.9 | Max Gas 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
REX 25 | 250 | 215000 | 272 | 2 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
REX 30 | 300 | 258000 | 325 | 2 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
REX 35 | 350 | 301000 | 380 | 2.9 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
REX 40 | 400 | 344000 | 434 | 4.1 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
REX 50 | 500 | 430000 | 542 | 4.2 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 70 | ------ | PAB | PR * | TL - LONG
REX 62 | 620 | 533200 | 672 | 6.4 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
REX 75 | 750 | 645000 | 813 | 5.2 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
REX 85 | 850 | 731000 | 921 | 7.2 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor 140 | ------ | PAB | PR * | TL - LONG
REX 95 | 950 | 817000 | 1030 | 5.2 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor 140 | ------ | PAB | PR * | TL - LONG
REX 100 | 1020 | 877200 | 1106 | 4 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor 140 | ------ | PAB | PR * | TL - LONG
REX 120 | 1200 | 1032000 | 1301 | 5.5 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 150.1 | ------ | PAB | PR * | TL - LONG | Multicalor 170.1 | ------ | PAB | PR * | TL - LONG
REX 130 | 1300 | 1118000 | 1409 | 6.5 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 150.1 | ------ | PAB | PR * | TL - LONG | Multicalor 170.1 | ------ | PAB | PR * | TL - LONG
REX 140 | 1400 | 1204000 | 1517 | 6 | Blu 1700.1 | ------ | PAB | PR * | TL - LONG | Maior P 150.1 | ------ | PAB | PR * | TL - LONG | Multicalor 170.1 | ------ | PAB | PR * | TL - LONG
REX 160 | 1600 | 1376000 | 1733 | 6.5 | Blu 2000.1 | ------ | PAB | PR * | TL - LONG | Maior P 200.1 | ------ | PAB | PR * | TL - LONG | Multicalor 200.1 | ------ | PAB | PR * | TL - LONG
REX 180 | 1800 | 1548000 | 1950 | 7 | Blu 3000.1 | ------ | ------ | PR * | TL - LONG | Maior P 200.1 | ------ | PAB | PR * | TL - LONG | Multicalor 200.1 | ------ | PAB | PR * | TL - LONG
REX 200 | 2000 | 1720000 | 2167 | 6 | Blu 3000.1 | ------ | ------ | PR * | TL - LONG | Maior P 300.1 | ------ | PAB | PR * | TL - LONG | Multicalor 300.1 | ------ | PAB | PR * | TL - LONG
REX 240 | 2400 | 2064000 | 2600 | 7.5 | Blu 3000.1 | ------ | ------ | PR * | TL - LONG | Maior P 300.1 | ------ | PAB | PR * | TL - LONG | Multicalor 300.1 | ------ | PAB | PR * | TL - LONG
REX 300 | 3000 | 2580000 | 3250 | 8 | Blu 4000.1 | ------ | ------ | PR * | TL - LONG | Maior P 400.1 | ------ | PAB | PR * | TL - LONG | Multicalor 400.1 | ------ | PAB | PR * | TL - LONG
REX 350 | 3500 | 3010000 | 3792 | 9 | Blu 5000.1 | ------ | ------ | PR * | TL - LONG | Maior P 500.1 | ------ | PAB | PR * | TL - LONG | Multicalor 500.1 | ------ | ------ | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI - REX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
REX 7 | 70 | 60200 | 76 | 0.8 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 8 | 80 | 68800 | 87 | 1 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 9 | 90 | 77400 | 98 | 0.8 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 10 | 100 | 86000 | 109 | 1 | Oilflam 15.1 | P | PAB | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 12 | 120 | 103200 | 131 | 1.1 | Oilflam 15.1 | P | PAB | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 15 | 150 | 129000 | 163 | 1.2 | Oilflam 15.1 | P | PAB | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 20 | 200 | 172000 | 218 | 1.9 | Oilflam 20.1 | P | PAB | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 25 | 250 | 215000 | 272 | 2 | Oilflam 30.1 | P | PAB | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
REX 30 | 300 | 258000 | 325 | 2 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | ------ | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
REX 35 | 350 | 301000 | 380 | 2.9 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
REX 40 | 400 | 344000 | 434 | 4.1 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
REX 50 | 500 | 430000 | 542 | 4.2 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
REX 62 | 620 | 533200 | 672 | 6.4 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
REX 75 | 750 | 645000 | 813 | 5.2 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
REX 85 | 850 | 731000 | 921 | 7.2 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
REX 95 | 950 | 817000 | 1030 | 5.2 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
REX 100 | 1020 | 877200 | 1106 | 4 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
REX 120 | 1200 | 1032000 | 1301 | 5.5 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 170.1 | ------ | PAB | PR * | TL - LONG
REX 130 | 1300 | 1118000 | 1409 | 6.5 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 170.1 | ------ | PAB | PR * | TL - LONG
REX 140 | 1400 | 1204000 | 1517 | 6 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 170.1 | ------ | PAB | PR * | TL - LONG
REX 160 | 1600 | 1376000 | 1733 | 6.5 | Oilflam 200.1 | ------ | PAB | PR * | TL - LONG | Oilflam 200.1 | ------ | PAB | PR * | TL - LONG | Multiflam 200.1 | ------ | PAB | PR * | TL - LONG
REX 180 | 1800 | 1548000 | 1950 | 7 | Oilflam 200.1 | ------ | ------ | PR * | TL - LONG | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Multiflam 200.1 | ------ | PAB | PR * | TL - LONG
REX 200 | 2000 | 1720000 | 2167 | 6 | Oilflam 300.1 | ------ | ------ | PR * | TL - LONG | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Multiflam 300.1 | ------ | PAB | PR * | TL - LONG
REX 240 | 2400 | 2064000 | 2600 | 7.5 | Oilflam 300.1 | ------ | ------ | PR * | TL - LONG | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Multiflam 300.1 | ------ | PAB | PR * | TL - LONG
REX 300 | 3000 | 2580000 | 3250 | 8 | Oilflam 400.1 | ------ | ------ | PR * | TL - LONG | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Multiflam 400.1 | ------ | PAB | PR * | TL - LONG
REX 350 | 3500 | 3010000 | 3792 | 9 | Oilflam 500.1 | ------ | ------ | PR * | TL - LONG | Oilflam 500.1 | ------ | PAB | PR * | TL - LONG | Multiflam 500.1 | ------ | ------ | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ICI PX - BX
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI PX - ICI BX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
PX 100 | 67 | 57620 | 77 | 1.5 | Max Gas 105 | P | PAB | PR * | TL - LONG | Max P 8 | P | PAB | ----- | EXTRA TL | Dual 3 P | P | ----- | ----- | TL - LONG
PX 150 | 101 | 86860 | 115 | 1.8 | Max Gas 170 | P | PAB | PR * | TL - LONG | Max P 15 | P | PAB | ----- | TL - LONG | Dual 4 P | P | ----- | ----- | TL - LONG
PX 200 | 135 | 116100 | 155 | 2.5 | Max Gas 170 | P | PAB | PR * | TL - LONG | Max P 15 | P | PAB | ----- | TL - LONG | Dual 5 P | P | ----- | ----- | TC - SHORT
PX 300 | 202 | 173720 | 233 | 3 | Blu 350 | P | PAB | PR * | TL - LONG | Max P 25 | P | PAB | ----- | TL - LONG | Dual 5 P | P | ----- | ----- | TC - SHORT
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
BX 60 | 70 | 60200 | 76 | 0.7 | Max Gas 105 | P | PAB | PR * | TL - LONG | Max P 8 | P | PAB | ----- | EXTRA TL | Dual 3 P | P | ----- | ----- | TL - LONG
BX 90 | 105 | 90300 | 116 | 1.5 | Max Gas 170 | P | PAB | PR * | TL - LONG | Max P 12 | P | PAB | ----- | EXTRA TL | Dual 4 P | P | ----- | ----- | TL - LONG
BX 200 | 233 | 200380 | 258 | 3.5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior 35 | P | PAB | ----- | TL - LONG | Dual 5 P | P | ----- | ----- | TL - LONG
BX 300 | 349 | 300140 | 387 | 5 | Blu 500 | P | PAB | PR * | TL - LONG | Maior 45 | P | PAB | PR * | TL - LONG | Multicalor 45 | ----- | PAB | PR * | TL - LONG
BX 400 | 465 | 399900 | 516 | 5 | Blu 700 | P | PAB | PR * | TL - LONG | Maior 60 | P | PAB | PR * | TL - LONG | Multicalor 70 | ----- | PAB | PR * | TL - LONG
BX 500 | 581 | 499660 | 645 | 4.5 | Blu 1000 | ----- | ----- | PR * | TL - LONG | Maior 80 | ----- | PAB | PR * | TL - LONG | Multicalor 100 | ----- | PAB | PR * | TL - LONG
BX 600 | 698 | 600280 | 774 | 6 | Blu 1000 | ----- | ----- | PR * | TL - LONG | Maior 80 | ----- | PAB | PR * | TL - LONG | Multicalor 100 | ----- | PAB | PR * | TL - LONG
BX 800 | 930 | 799800 | 1032 | 5.5 | Blu 1400 | ----- | ----- | PR * | TL - LONG | Maior 120 | ----- | PAB | PR * | TL - LONG | Multicalor 140 | ----- | PAB | PR * | TL - LONG
BX 1000 | 1163 | 1000180 | 1292 | 7 | Blu 1700.1 R | ----- | ----- | PR * | TL - LONG | Maior 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor 170.1 | ----- | PAB | PR * | TL - LONG
BX 1200 | 1395 | 1199700 | 1550 | 7.5 | Blu 1700.1 | ----- | ----- | PR * | TL - LONG | Maior 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor 170.1 | ----- | PAB | PR * | TL - LONG
BX 1500 | 1744 | 1499840 | 1937 | 6.5 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor 300.1 | ----- | PAB | PR * | TL - LONG
BX 1750 | 2035 | 1750100 | 2260 | 7.5 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor 300.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI PX - ICI BX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
PX 100 | 67 | 57620 | 77 | 1.5 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
PX 150 | 101 | 86860 | 115 | 1.8 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
PX 200 | 135 | 116100 | 155 | 2.5 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
PX 300 | 202 | 173720 | 233 | 3 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
BX 60 | 70 | 60200 | 76 | 0.7 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
BX 90 | 105 | 90300 | 116 | 1.5 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
BX 200 | 233 | 200380 | 258 | 3.5 | Oilflam 30.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
BX 300 | 349 | 300140 | 387 | 5 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
BX 400 | 465 | 399900 | 516 | 5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 70 | ----- | PAB | PR * | TL - LONG
BX 500 | 581 | 499660 | 645 | 4.5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
BX 600 | 698 | 600280 | 774 | 6 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
BX 800 | 930 | 799800 | 1032 | 5.5 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
BX 1000 | 1163 | 1000180 | 1292 | 7 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
BX 1200 | 1395 | 1199700 | 1550 | 7.5 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
BX 1500 | 1744 | 1499840 | 1937 | 6.5 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
BX 1750 | 2035 | 1750100 | 2260 | 7.5 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ICI AX
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI AX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
AX 200 | 233 | 200380 | 260 | 3,5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ----- | TL - LONG | Dual 5 P | P | ----- | ----- | TL - LONG
AX 300 | 349 | 300140 | 391 | 3,5 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ----- | PAB | PR * | TL - LONG | Multicalor P 45 | ----- | PAB | PR * | TL - LONG
AX 400 | 465 | 399900 | 522 | 5 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor P 70 | ----- | PAB | PR * | TL - LONG
AX 500 | 581 | 499660 | 652 | 4,5 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 80 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
AX 600 | 698 | 600280 | 784 | 6 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 80 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
AX 800 | 930 | 799800 | 1045 | 5,5 | Blu 1400 | ----- | PAB | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor P 140 | ----- | PAB | PR * | TL - LONG
AX 1000 | 1163 | 1000180 | 1306 | 7 | Blu 1700.1 R | ----- | PAB | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
AX 1200 | 1395 | 1199700 | 1567 | 8 | Blu 1700.1 | ----- | PAB | PR * | TL - LONG | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
AX 1500 | 1744 | 1499840 | 1959 | 6,5 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
AX 1750 | 2035 | 1750100 | 2286 | 7,5 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
AX 2000 | 2326 | 2000360 | 2612 | 8 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
AX 2500 | 2907 | 2500020 | 3266 | 9 | Blu 4000.1 | ----- | ----- | PR * | TL - LONG | Maior P 400.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 400.1 | ----- | PAB | PR * | TL - LONG
AX 3000 | 3488 | 2999680 | 3919 | 9,5 | Blu 5000.1 | ----- | ----- | PR * | TL - LONG | Maior P 500.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 500.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI AX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
AX 200 | 233 | 200380 | 260 | 3,5 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | ----- | TL - LONG | Multiflam P 50 | ----- | PAB | PR * | TL - LONG
AX 300 | 349 | 300140 | 391 | 3,5 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 50 | ----- | PAB | PR * | TL - LONG
AX 400 | 465 | 399900 | 522 | 5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 70 | ----- | PAB | PR * | TL - LONG
AX 500 | 581 | 499660 | 652 | 4,5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 120 | ----- | PAB | PR * | TL - LONG
AX 600 | 698 | 600280 | 784 | 6 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 120 | ----- | PAB | PR * | TL - LONG
AX 800 | 930 | 799800 | 1045 | 5,5 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 120 | ----- | PAB | PR * | TL - LONG
AX 1000 | 1163 | 1000180 | 1306 | 7 | Oilflam P 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam P 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 170.1 | ----- | PAB | PR * | TL - LONG
AX 1200 | 1395 | 1199700 | 1567 | 8 | Oilflam P 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam P 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 170.1 | ----- | PAB | PR * | TL - LONG
AX 1500 | 1744 | 1499840 | 1959 | 6,5 | Oilflam P 200.1 | ----- | PAB | PR * | TL - LONG | Oilflam P 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 300.1 | ----- | PAB | PR * | TL - LONG
AX 1750 | 2035 | 1750100 | 2286 | 7,5 | Oilflam P 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam P 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 300.1 | ----- | PAB | PR * | TL - LONG
AX 2000 | 2326 | 2000360 | 2612 | 8 | Oilflam P 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam P 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 300.1 | ----- | PAB | PR * | TL - LONG
AX 2500 | 2907 | 2500020 | 3266 | 9 | Oilflam P 400.1 | ----- | PAB | PR * | TL - LONG | Oilflam P 400.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 400.1 | ----- | ----- | PR * | TL - LONG
AX 3000 | 3488 | 2999680 | 3919 | 9,5 | Oilflam P 500.1 | ----- | PAB | PR * | TL - LONG | Oilflam P 500.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 500.1 | ----- | ----- | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ICI ASX
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI ASX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | DUAL FUEL BURNER
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
ASX 200 | 233 | 200380 | 260 | 3,5 | Blu 350 | PAB | PR * | TL - LONG | Maior P 35 | PAB | ----- | TL - LONG | Dual 5 P | ----- | ----- | TL - LONG
ASX 300 | 349 | 300140 | 391 | 3,5 | Blu 500 | PAB | PR * | TL - LONG | Maior P 45 | PAB | PR * | TL - LONG | Multicalor P 45 | PAB | PR * | TL - LONG
ASX 400 | 465 | 399900 | 522 | 5 | Blu 700 | PAB | PR * | TL - LONG | Maior P 60 | PAB | PR * | TL - LONG | Multicalor P 70 | PAB | PR * | TL - LONG
ASX 500 | 581 | 499660 | 652 | 4,5 | Blu 1000 | PAB | PR * | TL - LONG | Maior P 80 | PAB | PR * | TL - LONG | Multicalor P 100 | PAB | PR * | TL - LONG
ASX 600 | 698 | 600280 | 784 | 6 | Blu 1000 | PAB | PR * | TL - LONG | Maior P 80 | PAB | PR * | TL - LONG | Multicalor P 100 | PAB | PR * | TL - LONG
ASX 800 | 930 | 799800 | 1045 | 5,5 | Blu 1400 | PAB | PR * | TL - LONG | Maior P 120 | PAB | PR * | TL - LONG | Multicalor P 140 | PAB | PR * | TL - LONG
ASX 1000 | 1163 | 1000180 | 1306 | 7 | Blu 1700.1 R | PAB | PR * | TL - LONG | Maior P 150.1 | PAB | PR * | TL - LONG | Multicalor P 170.1 | PAB | PR * | TL - LONG
ASX 1200 | 1395 | 1199700 | 1567 | 8 | Blu 2000.1 | PAB | PR * | TL - LONG | Maior P 200.1 | PAB | PR * | TL - LONG | Multicalor P 200.1 | PAB | PR * | TL - LONG
ASX 1500 | 1744 | 1499840 | 1959 | 6,5 | Blu 3000.1 | ----- | PR * | TL - LONG | Maior P 200.1 | PAB | PR * | TL - LONG | Multicalor P 300.1 | PAB | PR * | TL - LONG
ASX 1750 | 2035 | 1750100 | 2286 | 7,5 | Blu 3000.1 | ----- | PR * | TL - LONG | Maior P 300.1 | PAB | PR * | TL - LONG | Multicalor P 300.1 | PAB | PR * | TL - LONG
ASX 2000 | 2326 | 2000360 | 2612 | 8 | Blu 3000.1 | ----- | PR * | TL - LONG | Maior P 400.1 | PAB | PR * | TL - LONG | Multicalor P 300.1 | PAB | PR * | TL - LONG
ASX 2500 | 2907 | 2500020 | 3266 | 9 | Blu 4000.1 | ----- | PR * | TL - LONG | Maior P 400.1 | PAB | PR * | TL - LONG | Multicalor P 400.1 | PAB | PR * | TL - LONG
ASX 3000 | 3488 | 2999680 | 3919 | 9,5 | Blu 5000.1 | ----- | PR * | TL - LONG | Maior P 500.1 | PAB | PR * | TL - LONG | Multicalor P 500.1 | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI ASX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
ASX 200 | 233 | 200380 | 260 | 3,5 | Oilflam 50.1 | PAB | PR * | TL - LONG | Oilflam 50.1 | PAB | PR * | TL - LONG | Multiflam P 50 | ----- | PR * | TL - LONG
ASX 300 | 349 | 300140 | 391 | 3,5 | Oilflam 50.1 | PAB | PR * | TL - LONG | Oilflam 50.1 | PAB | PR * | TL - LONG | Multiflam P 50 | PAB | PR * | TL - LONG
ASX 400 | 465 | 399900 | 522 | 5 | Oilflam 80.1 | PAB | PR * | TL - LONG | Oilflam 80.1 | PAB | PR * | TL - LONG | Multiflam P 70 | PAB | PR * | TL - LONG
ASX 500 | 581 | 499660 | 652 | 4,5 | Oilflam 80.1 | PAB | PR * | TL - LONG | Oilflam 80.1 | PAB | PR * | TL - LONG | Multiflam P 120 | PAB | PR * | TL - LONG
ASX 600 | 698 | 600280 | 784 | 6 | Oilflam 120.1 | PAB | PR * | TL - LONG | Oilflam 120.1 | PAB | PR * | TL - LONG | Multiflam P 120 | PAB | PR * | TL - LONG
ASX 800 | 930 | 799800 | 1045 | 5,5 | Oilflam 120.1 | PAB | PR * | TL - LONG | Oilflam 120.1 | PAB | PR * | TL - LONG | Multiflam P 120 | PAB | PR * | TL - LONG
ASX 1000 | 1163 | 1000180 | 1306 | 7 | Oilflam 170.1 | PAB | PR * | TL - LONG | Oilflam 170.1 | PAB | PR * | TL - LONG | Multiflam P 170.1 | PAB | PR * | TL - LONG
ASX 1200 | 1395 | 1199700 | 1567 | 8 | Oilflam 170.1 | PAB | PR * | TL - LONG | Oilflam 170.1 | PAB | PR * | TL - LONG | Multiflam P 170.1 | PAB | PR * | TL - LONG
ASX 1500 | 1744 | 1499840 | 1959 | 6,5 | Oilflam 200.1 | PAB | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam P 300.1 | PAB | PR * | TL - LONG
ASX 1750 | 2035 | 1750100 | 2286 | 7,5 | Oilflam 300.1 | PAB | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam P 300.1 | PAB | PR * | TL - LONG
ASX 2000 | 2326 | 2000360 | 2612 | 8 | Oilflam 300.1 | PAB | PR * | TL - LONG | Oilflam 300.1 | PAB | PR * | TL - LONG | Multiflam P 300.1 | PAB | PR * | TL - LONG
ASX 2500 | 2907 | 2500020 | 3266 | 9 | Oilflam 400.1 | PAB | PR * | TL - LONG | Oilflam 400.1 | PAB | PR * | TL - LONG | Multiflam P 400.1 | PAB | PR * | TL - LONG
ASX 3000 | 3488 | 2999680 | 3919 | 9,5 | Oilflam 500.1 | PAB | PR * | TL - LONG | Oilflam 500.1 | PAB | PR * | TL - LONG | Multiflam P 500.1 | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ICI GX
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI GX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | DUAL FUEL BURNER
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
GX 1000 | 1162 | 999320 | 1305 | 5.5 | Blu 1700.1 R | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Maior P 150.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Multicalor P 170.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer
GX 1200 | 1395 | 1199700 | 1567 | 7 | Blu 1700.1 | PAB | PR * |  | Maior P 150.1 | PAB | PR * |  | Multicalor P 170.1 | PAB | PR *
GX 1500 | 1744 | 1499840 | 1959 | 7 | Blu 3000.1 | ----- | PR * |  | Maior P 200.1 | PAB | PR * |  | Multicalor P 300.1 | PAB | PR *
GX 1750 | 2035 | 1750100 | 2286 | 7 | Blu 3000.1 | ----- | PR * |  | Maior P 300.1 | PAB | PR * |  | Multicalor P 300.1 | PAB | PR *
GX 2000 | 2326 | 2000360 | 2612 | 8.5 | Blu 3000.1 | ----- | PR * |  | Maior P 300.1 | PAB | PR * |  | Multicalor P 300.1 | PAB | PR *
GX 2500 | 2907 | 2500020 | 3266 | 8 | Blu 4000.1 | ----- | PR * |  | Maior P 400.1 | PAB | PR * |  | Multicalor P 400.1 | PAB | PR *
GX 3000 | 3488 | 2999680 | 3919 | 9 | Blu 5000.1 | ----- | PR * |  | Maior P 500.1 | PAB | PR * |  | Multicalor P 500.1 | PAB | PR *
GX 3500 | 4070 | 3500200 | 4572 | 10.5 | Blu 6000.1 | ----- | PR * |  | Maior P 600.1 | PAB | PR * |  | Multicalor P 600.1 | PAB | PR *
GX 4000 | 4651 | 3999860 | 5225 | 10 | Blu 7000.1 | ----- | PR * |  | Maior P 700.1 | ----- | PR * |  | Multicalor P 700.1 | ----- | PR *
GX 5000 | 5814 | 5000040 | 6531 | 10.5 | Blu 8000.1 | ----- | PR * |  | Maior P 800.1 | ----- | PR * |  | Multicalor P 800.1 | ----- | PR *
GX 6000 | 6977 | 6000220 | 7838 | 12 | Blu 8000.1 | ----- | PR * |  | Maior P 800.1 | ----- | PR * |  | Multicalor P 800.1 | ----- | PR *
GX 7000 | 8140 | 7000400 | 9145 | 12 | Blu 10000.1 | ----- | PR * |  | Maior P 1000.1 | ----- | PR * |  | Multicalor P 1000.1 | ----- | PR *
GX 8000 | 9302 | 7999720 | 10451 | 14 | Blu 12000.1 | ----- | PR * |  | Maior P 1200.1 | ----- | PR * |  | Multicalor P 1200.1 | ----- | PR *
GX 9000 | 10465 | 8999900 | 11758 | 14 | Blu 15000.1 | ----- | PR * |  | Maior P 1500.1 | ----- | PR * |  | Multicalor P 1500.1 | ----- | PR *
GX 10000 | 11628 | 10000080 | 13063 | 15 | Blu 15000.1 | ----- | PR * |  | Maior P 1500.1 | ----- | PR * |  | Multicalor P 1500.1 | ----- | PR *
GX 12000 | 13953 | 11999580 | 15250 | 17 | Blu 15000.1 | ----- | PR * |  | Maior P 1500.1 | ----- | PR * |  | Multicalor P 1500.1 | ----- | PR *
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI GX
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
GX 1000 | 1162 | 999320 | 1305 | 5.5 | Oilflam P 170.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Oilflam P 170.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Multiflam P 170.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer
GX 1200 | 1395 | 1199700 | 1567 | 7 | Oilflam P 170.1 | PAB | PR * |  | Oilflam P 170.1 | PAB | PR * |  | Multiflam P 170.1 | PAB | PR *
GX 1500 | 1744 | 1499840 | 1959 | 7 | Oilflam P 200.1 | PAB | PR * |  | Oilflam P 200.1 | PAB | PR * |  | Multiflam P 300.1 | PAB | PR *
GX 1750 | 2035 | 1750100 | 2286 | 7 | Oilflam P 300.1 | PAB | PR * |  | Oilflam P 300.1 | PAB | PR * |  | Multiflam P 300.1 | PAB | PR *
GX 2000 | 2326 | 2000360 | 2612 | 8.5 | Oilflam P 300.1 | PAB | PR * |  | Oilflam P 400.1 | PAB | PR * |  | Multiflam P 300.1 | PAB | PR *
GX 2500 | 2907 | 2500020 | 3266 | 8 | Oilflam P 400.1 | PAB | PR * |  | Oilflam P 400.1 | PAB | PR * |  | Multiflam P 400.1 | PAB | PR *
GX 3000 | 3488 | 2999680 | 3919 | 9 | Oilflam P 500.1 | PAB | PR * |  | Oilflam P 500.1 | PAB | PR * |  | Multiflam P 500.1 | PAB | PR *
GX 3500 | 4070 | 3500200 | 4572 | 10.5 | Oilflam P 600.1 | PAB | PR * |  | Oilflam P 600.1 | PAB | PR * |  | Multiflam P 600.1 | PAB | PR *
GX 4000 | 4651 | 3999860 | 5225 | 10 | Oilflam P 700.1 | ----- | PR * |  | Oilflam P 700.1 | ----- | PR * |  | Multiflam P 700.1 | ----- | PR *
GX 5000 | 5814 | 5000040 | 6531 | 10.5 | Oilflam P 800.1 | ----- | PR * |  | Oilflam P 800.1 | ----- | PR * |  | Multiflam P 800.1 | ----- | PR *
GX 6000 | 6977 | 6000220 | 7838 | 12 | Oilflam P 800.1 | ----- | PR * |  | Oilflam P 800.1 | ----- | PR * |  | Multiflam P 800.1 | ----- | PR *
GX 7000 | 8140 | 7000400 | 9145 | 12 | Oilflam P 1000.1 | ----- | PR * |  | Oilflam P 1000.1 | ----- | PR * |  | Multiflam P 1000.1 | ----- | PR *
GX 8000 | 9302 | 7999720 | 10451 | 14 | Oilflam P 1200.1 | ----- | PR * |  | Oilflam P 1200.1 | ----- | PR * |  | Multiflam P 1200.1 | ----- | PR *
GX 9000 | 10465 | 8999900 | 11758 | 14 | Oilflam P 1500.1 | ----- | PR * |  | Oilflam P 1500.1 | ----- | PR * |  | Multiflam P 1500.1 | ----- | PR *
GX 10000 | 11628 | 10000080 | 13063 | 15 | Oilflam P 1500.1 | ----- | PR * |  | Oilflam P 1500.1 | ----- | PR * |  | Multiflam P 1500.1 | ----- | PR *
GX 12000 | 13953 | 11999580 | 15250 | 17 | Oilflam P 1500.1 | ----- | PR * |  | Oilflam P 1500.1 | ----- | PR * |  | Multiflam P 1500.1 | ----- | PR *
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ICI TNG
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI TNG
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | DUAL FUEL BURNER
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
TNG 1700 | 1977 | 1700220 | 1959 | 7 | Blu 3000.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Maior P 200.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Multicalor P 300.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer
TNG 2000 | 2326 | 2000360 | 2612 | 8.5 | Blu 3000.1 | PAB | PR * |  | Maior P 300.1 | PAB | PR * |  | Multicalor P 300.1 | PAB | PR *
TNG 2500 | 2907 | 2500020 | 3266 | 8 | Blu 4000.1 | PAB | PR * |  | Maior P 400.1 | PAB | PR * |  | Multicalor P 400.1 | PAB | PR *
TNG 3000 | 3488 | 2999680 | 3919 | 9 | Blu 5000.1 | PAB | PR * |  | Maior P 500.1 | PAB | PR * |  | Multicalor P 500.1 | ----- | PR *
TNG 3500 | 4070 | 3500200 | 4572 | 10.5 | Blu 6000.1 | PAB | PR * |  | Maior P 600.1 | PAB | PR * |  | Multicalor P 600.1 | ----- | PR *
TNG 4000 | 4651 | 3999860 | 5225 | 10 | Blu 7000.1 | PAB | PR * |  | Maior P 700.1 | PAB | PR * |  | Multicalor P 700.1 | ----- | PR *
TNG 5000 | 5814 | 5000040 | 6531 | 10.5 | Blu 8000.1 | PAB | PR * |  | Maior P 800.1 | PAB | PR * |  | Multicalor P 800.1 | ----- | PR *
TNG 6000 | 6977 | 6000220 | 7838 | 12 | Blu 8000.1 | PAB | PR * |  | Maior P 800.1 | PAB | PR * |  | Multicalor P 800.1 | ----- | PR *
TNG 7000 | 8140 | 7000400 | 9145 | 12 | Blu 10000.1 | PAB | PR * |  | Maior P 1000.1 | PAB | PR * |  | Multicalor P 1000.1 | ----- | PR *
TNG 8000 | 9302 | 7999720 | 10451 | 14 | Blu 12000.1 | ----- | PR * |  | Maior P 1200.1 | ----- | PR * |  | Multicalor P 1200.1 | ----- | PR *
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI TNG
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
TNG 1700 | 1977 | 1700220 | 1959 | 7 | Oilflam 200.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Oilflam 300.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer | Multiflam P 300.1 | PAB | PR * | Blast tube according to the specifics of burner and boiler manufacturer
TNG 2000 | 2326 | 2000360 | 2612 | 8.5 | Oilflam 300.1 | PAB | PR * |  | Oilflam 300.1 | PAB | PR * |  | Multiflam P 300.1 | PAB | PR *
TNG 2500 | 2907 | 2500020 | 3266 | 8 | Oilflam 400.1 | PAB | PR * |  | Oilflam 400.1 | PAB | PR * |  | Multiflam P 400.1 | ----- | PR *
TNG 3000 | 3488 | 2999680 | 3919 | 9 | Oilflam 500.1 | PAB | PR * |  | Oilflam 500.1 | PAB | PR * |  | Multiflam P 500.1 | ----- | PR *
TNG 3500 | 4070 | 3500200 | 4572 | 10.5 | Oilflam 600.1 | PAB | PR * |  | Oilflam 600.1 | PAB | PR * |  | Multiflam P 600.1 | ----- | PR *
TNG 4000 | 4651 | 3999860 | 5225 | 10 | Oilflam 700.1 | ----- | PR * |  | Oilflam 700.1 | ----- | PR * |  | Multiflam P 700.1 | ----- | PR *
TNG 5000 | 5814 | 5000040 | 6531 | 10.5 | Oilflam 800.1 | ----- | PR * |  | Oilflam 800.1 | ----- | PR * |  | Multiflam P 800.1 | ----- | PR *
TNG 6000 | 6977 | 6000220 | 7838 | 12 | Oilflam 800.1 | ----- | PR * |  | Oilflam 800.1 | ----- | PR * |  | Multiflam P 800.1 | ----- | PR *
TNG 7000 | 8140 | 7000400 | 9145 | 12 | Oilflam 1000.1 | ----- | PR * |  | Oilflam 1000.1 | ----- | PR * |  | Multiflam P 1000.1 | ----- | PR *
TNG 8000 | 9302 | 7999720 | 10451 | 14 | Oilflam 1200.1 | ----- | PR * |  | Oilflam 1200.1 | ----- | PR * |  | Multiflam P 1200.1 | ----- | PR *
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## ICI OPX
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI OPX - ICI OPX REC
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
OPX 100 | 116 | 99760 | 135 | 1 | Max Gas 170 | P | PAB | PR * | TL - LONG | Max P 15 | P | PAB | --- | TL - LONG | Dual 4 P | P | --- | --- | TL - LONG
OPX 200 | 233 | 200380 | 273 | 1.5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | --- | TL - LONG | Dual 5 P | P | --- | --- | TL - LONG
OPX 300 | 349 | 300140 | 405 | 2 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | P | PAB | PR * | TL - LONG | Multicalor P 45 | P | PAB | PR * | TL - LONG
OPX 400 | 465 | 399900 | 541 | 3 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | P | PAB | PR * | TL - LONG | Multicalor P 70 | P | PAB | PR * | TL - LONG
OPX 500 | 581 | 499660 | 676 | 3 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
OPX 600 | 698 | 600280 | 810 | 4 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 80 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
OPX 800 | 930 | 799800 | 1081 | 4.5 | Blu 1400 | ----- | PAB | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor P 140 | ----- | PAB | PR * | TL - LONG
OPX 1000 | 1163 | 1000180 | 1351 | 4.5 | Blu 1700.1 R | ----- | PAB | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
OPX 1200 | 1395 | 1199700 | 1622 | 7 | Blu 2000.1 | ----- | PAB | PR * | TL - LONG | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 200.1 | ----- | PAB | PR * | TL - LONG
OPX 1500 | 1744 | 1499840 | 2028 | 8 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
OPX 1000 REC | 1163 | 1000180 | 1277 | 4.5 | Blu 1700.1 R | PAB | PAB | PR * | Blust tube according to the specifics of burner and boiler manufacturer | Maior P 150.1 | PAB | PAB | PR * | Blust tube according to the specifics of burner and boiler manufacturer | Multicalor P 170.1 | PAB | PAB | PR * | Blust tube according to the specifics of burner and boiler manufacturer
OPX 1200 REC | 1395 | 1199700 | 1533 | 7 | Blu 1700.1 | PAB | PAB | PR * |  | Maior P 200.1 | PAB | PAB | PR * |  | Multicalor P 170.1 | PAB | PAB | PR *
OPX 1500 REC | 1744 | 1499840 | 1916 | 8 | Blu 3000.1 | PAB | PAB | PR * |  | Maior P 200.1 | PAB | PAB | PR * |  | Multicalor P 300.1 | PAB | PAB | PR *
OPX 2000 REC | 2326 | 2000360 | 2555 | 8 | Blu 3000.1 | ----- | PAB | PR * |  | Maior P 300.1 | ----- | PAB | PR * |  | Multicalor P 300.1 | ----- | PAB | PR *
OPX 2500 REC | 2907 | 2500020 | 3194 | 9 | Blu 4000.1 | ----- | ----- | PR * |  | Maior P 400.1 | ----- | PAB | PR * |  | Multicalor P 400.1 | ----- | PAB | PR *
OPX 3000 REC | 3488 | 2999680 | 3833 | 10 | Blu 5000.1 | ----- | ----- | PR * |  | Maior P 500.1 | ----- | PAB | PR * |  | Multicalor P 500.1 | ----- | PAB | PR *
OPX 4000 REC | 4651 | 3999860 | 5110 | 12 | Blu 7000.1 | ----- | ----- | PR * |  | Maior P 700.1 | ----- | ----- | PR * |  | Multicalor P 700.1 | ----- | ----- | PR *
OPX 5000 REC | 5814 | 5000040 | 6388 | 15 | Blu 8000.1 | ----- | ----- | PR * |  | Maior P 800.1 | ----- | ----- | PR * |  | Multicalor P 800.1 | ----- | ----- | PR *
OPX 6000 REC | 6977 | 6000220 | 7666 |  | Blu 8000.1 | ----- | ----- | PR * |  | Maior P 800.1 | ----- | ----- | PR * |  | Multicalor P 800.1 | ----- | ----- | PR *
OPX 8000 REC | 9302 | 7999720 | 10222 |  | Blu 12000.1 | ----- | ----- | PR * |  | Maior P 1200.1 | ----- | ----- | PR * |  | Multicalor P 1200.1 | ----- | ----- | PR *
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ICI OPX - ICI OPX REC
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
OPX 100 | 116 | 99760 | 135 | 1 | Oilflam 15.1 | P | PAB | --- | TL - LONG | Oilflam 15.1 | P | PAB | --- | TL - LONG | ----------------- | ----- | ----- | ----- | TL - LONG
OPX 200 | 233 | 200380 | 273 | 1.5 | Oilflam 30.1 | P | PAB | --- | TL - LONG | Oilflam 30.1 | P | PAB | --- | TL - LONG | ----------------- | ----- | ----- | ----- | TL - LONG
OPX 300 | 349 | 300140 | 405 | 2 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 50 | ----- | PAB | PR * | TL - LONG
OPX 400 | 465 | 399900 | 541 | 3 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 70 | ----- | PAB | PR * | TL - LONG
OPX 500 | 581 | 499660 | 676 | 3 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 120 | ----- | PAB | PR * | TL - LONG
OPX 600 | 698 | 600280 | 810 | 4 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 120 | ----- | PAB | PR * | TL - LONG
OPX 800 | 930 | 799800 | 1081 | 4.5 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 120 | ----- | PAB | PR * | TL - LONG
OPX 1000 | 1163 | 1000180 | 1351 | 4.5 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 170.1 | ----- | PAB | PR * | TL - LONG
OPX 1200 | 1395 | 1199700 | 1622 | 7 | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 200.1 | ----- | PAB | PR * | TL - LONG
OPX 1500 | 1744 | 1499840 | 2028 | 8 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam P 300.1 | ----- | PAB | PR * | TL - LONG
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
OPX 1000 REC | 1163 | 1000180 | 1277 | 4.5 | Oilflam 170.1 | ----- | PAB | PR * | Blust tube according to the specifics of burner and boiler manufacturer | Oilflam 170.1 | ----- | PAB | PR * | Blust tube according to the specifics of burner and boiler manufacturer | Multiflam P 170.1 | ----- | PAB | PR * | Blust tube according to the specifics of burner and boiler manufacturer
OPX 1200 REC | 1395 | 1199700 | 1533 | 7 | Oilflam 170.1 | ----- | PAB | PR * |  | Oilflam 170.1 | ----- | PAB | PR * |  | Multiflam P 200.1 | ----- | PAB | PR *
OPX 1500 REC | 1744 | 1499840 | 1916 | 8 | Oilflam 300.1 | ----- | PAB | PR * |  | Oilflam 300.1 | ----- | PAB | PR * |  | Multiflam P 300.1 | ----- | PAB | PR *
OPX 2000 REC | 2326 | 2000360 | 2555 | 8 | Oilflam 300.1 | ----- | PAB | PR * |  | Oilflam 300.1 | ----- | PAB | PR * |  | Multiflam P 300.1 | ----- | PAB | PR *
OPX 2500 REC | 2907 | 2500020 | 3194 | 9 | Oilflam 400.1 | ----- | PAB | PR * |  | Oilflam 400.1 | ----- | PAB | PR * |  | Multiflam P 400.1 | ----- | PAB | PR *
OPX 3000 REC | 3488 | 2999680 | 3833 | 10 | Oilflam 500.1 | ----- | PAB | PR * |  | Oilflam 500.1 | ----- | PAB | PR * |  | Multiflam P 500.1 | ----- | PAB | PR *
OPX 4000 REC | 4651 | 3999860 | 5110 | 12 | Oilflam 700.1 | ----- | ----- | PR * |  | Oilflam 700.1 | ----- | ----- | PR * |  | Multiflam P 700.1 | ----- | ----- | PR *
OPX 5000 REC | 5814 | 5000040 | 6388 | 15 | Oilflam 800.1 | ----- | ----- | PR * |  | Oilflam 800.1 | ----- | ----- | PR * |  | Multiflam P 800.1 | ----- | ----- | PR *
OPX 6000 REC | 6977 | 6000220 | 7666 |  | Oilflam 800.1 | ----- | ----- | PR * |  | Oilflam 800.1 | ----- | ----- | PR * |  | Multiflam P 800.1 | ----- | ----- | PR *
OPX 8000 REC | 9302 | 7999720 | 10222 |  | Oilflam 1200.1 | ----- | ----- | PR * |  | Oilflam 1200.1 | ----- | ----- | PR * |  | Multiflam P 1200.1 | ----- | ----- | PR *
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE