## IVAR SuperRAC
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - SuperRAC
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
SuperRAC 93 | 93 | 79980 | 103 | 0.5 | Max Gas 120 | P | PAB | PR * | TL - LONG | Max 12 | P | ------ | ------ | TL - EXTRA | Dual 3 P | P | ------ | ------ | TC - SHORT
SuperRAC 105 | 105 | 90300 | 115.5 | 0.7 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TC - SHORT
SuperRAC 150 | 150 | 129000 | 167 | 1.2 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TC - SHORT
SuperRAC 190 | 192 | 165120 | 211 | 1.2 | Max Gas 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
SuperRAC 230 | 233 | 200380 | 257 | 1.5 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
SuperRAC 290 | 291 | 250260 | 320 | 2.3 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
SuperRAC 345 | 349 | 300140 | 384 | 3.3 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Multicalor P 45 | ------ | PAB | PR * | TL - LONG
SuperRAC 405 | 407 | 350020 | 449 | 4.4 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Multicalor P 45 | ------ | PAB | PR * | TL - LONG
SuperRAC 465 | 465 | 399900 | 511 | 3.3 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor P 70 | ------ | PAB | PR * | TL - LONG
SuperRAC 520 | 523 | 449780 | 577 | 4.3 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor P 70 | ------ | PAB | PR * | TL - LONG
SuperRAC 580 | 581 | 499660 | 637 | 4.8 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor P 100 | ------ | PAB | PR * | TL - LONG
SuperRAC 695 | 700 | 602000 | 771 | 4.5 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor P 100 | ------ | PAB | PR * | TL - LONG
SuperRAC 810 | 820 | 705200 | 899 | 5.6 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor P 120 | ------ | PAB | PR * | TL - LONG
SuperRAC 930 | 940 | 808400 | 1027 | 5.4 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor P 120 | ------ | PAB | PR * | TL - LONG
SuperRAC 1045 | 1060 | 911600 | 1156 | 6 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 150.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 170.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 1220 | 1240 | 1066400 | 1349 | 6.5 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 150.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 170.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 1450 | 1480 | 1272800 | 1606 | 6.8 | Blu 2000.1 | ------ | PAB | PR * | TL - LONG | Maior P 200.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 200.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 1860 | 1890 | 1625400 | 2056 | 7 | Blu 3000.1 | ------ | PAB | PR * | TL - LONG | Maior P 300.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 300.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 2330 | 2360 | 2029600 | 2570 | 7.2 | Blu 3000.1 | ------ | PAB | PR * | TL - LONG | Maior P 300.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 300.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 2910 | 2960 | 2545600 | 3213 | 7.5 | Blu 4000.1 | ------ | PAB | PR * | TL - LONG | Maior P 400.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 400.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 3940 | 2550 | 2193000 | 3855 | 7.8 | Blu 5000.1 | ------ | PAB | PR * | TL - LONG | Maior P 500.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 500.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 4070 | 4150 | 3569000 | 4497 | 9 | Blu 6000.1 | ------ | ------ | PR * | TL - LONG | Maior P 600.1 | ------ | PAB | PR * | TL - LONG | Multicalor P 600.1 | ------ | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - SuperRAC
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
SuperRAC 93 | 93 | 79980 | 103 | 0.5 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ----------------- | ------ | ------ | ------ | --------------
SuperRAC 105 | 105 | 90300 | 115.5 | 0.7 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ----------------- | ------ | ------ | ------ | --------------
SuperRAC 150 | 150 | 129000 | 167 | 1.2 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ----------------- | ------ | ------ | ------ | --------------
SuperRAC 190 | 192 | 165120 | 211 | 1.2 | Oilflam 20.1 | P | ------ | ------ | TL - LONG | Oilflam 20.1 | P | ------ | ------ | TL - LONG | ----------------- | ------ | ------ | ------ | --------------
SuperRAC 230 | 233 | 200380 | 257 | 1.5 | Oilflam 30.1 | P | ------ | ------ | TL - LONG | Oilflam 30.1 | P | ------ | ------ | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
SuperRAC 290 | 291 | 250260 | 320 | 2.3 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
SuperRAC 345 | 349 | 300140 | 384 | 3.3 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
SuperRAC 405 | 407 | 350020 | 449 | 4.4 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
SuperRAC 465 | 465 | 399900 | 511 | 3.3 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
SuperRAC 520 | 523 | 449780 | 577 | 4.3 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
SuperRAC 580 | 581 | 499660 | 637 | 4.8 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
SuperRAC 695 | 700 | 602000 | 771 | 4.5 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
SuperRAC 810 | 820 | 705200 | 899 | 5.6 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
SuperRAC 930 | 940 | 808400 | 1027 | 5.4 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
SuperRAC 1045 | 1060 | 911600 | 1156 | 6 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
SuperRAC 1220 | 1240 | 1066400 | 1349 | 6.5 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 170.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 1450 | 1480 | 1272800 | 1606 | 6.8 | Oilflam 200.1 | ------ | PAB | PR * | TL - LONG | Oilflam 200.1 | ------ | PAB | PR * | TL - LONG | Multiflam 200.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 1860 | 1890 | 1625400 | 2056 | 7 | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Multiflam 300.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 2330 | 2360 | 2029600 | 2570 | 7.2 | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Multiflam 300.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 2910 | 2960 | 2545600 | 3213 | 7.5 | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Multiflam 400.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 3940 | 2550 | 2193000 | 3855 | 7.8 | Oilflam 500.1 | ------ | PAB | PR * | TL - LONG | Oilflam 500.1 | ------ | PAB | PR * | TL - LONG | Multiflam 500.1 | ------ | PAB | PR * | TL - LONG
SuperRAC 4070 | 4150 | 3569000 | 4497 | 9 | Oilflam 600.1 | ------ | PAB | PR * | TL - LONG | Oilflam 600.1 | ------ | PAB | PR * | TL - LONG | Multiflam 600.1 | ------ | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## IVAR Trispace
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - TRISPACE
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
TRISPACE 31 | 31.4 | 27004 | 34.9 | 0.2 | Max Gas 40 | P | ----- | ----- | TL - LONG | Max 1 | ------ | ------ | ------ | TL - LONG | Dual 2 P | P | ------ | ------ | TC - SHORT
TRISPACE 60 | 58 | 49880 | 64.4 | 0.4 | Max Gas 70 | P | PAB | PR * | TL - LONG | Max 8 | ------ | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TC - SHORT
TRISPACE 80 | 81 | 69660 | 89.7 | 0.6 | Max Gas 105 | P | PAB | PR * | TL - LONG | Max 8 | ------ | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TC - SHORT
TRISPACE 105 | 104.8 | 90128 | 115.8 | 0.7 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
TRISPACE 130 | 125 | 107500 | 138.3 | 1 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
TRISPACE 190 | 190 | 163400 | 209.9 | 1.5 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TC - SHORT
TRISPACE 230 | 226.5 | 194790 | 248.9 | 2.1 | Blu 350 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TC - SHORT
TRISPACE 260 | 255 | 219300 | 282.1 | 2.5 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | PAB | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
TRISPACE 345 | 340 | 292400 | 374 | 3.1 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | P | PAB | PR * | TC - SHORT | Multicalor P 45 | ------ | PAB | PR * | TL - LONG
TRISPACE 405 | 396.1 | 340646 | 432.9 | 3.9 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | P | PAB | PR * | TC - SHORT | Multicalor P 45 | ------ | PAB | PR * | TL - LONG
TRISPACE 440 | 440 | 378400 | 486.2 | 4.9 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | P | PAB | PR * | TC - SHORT | Multicalor P 70 | ------ | PAB | PR * | TL - LONG
TRISPACE 520 | 514.4 | 442384 | 562.2 | 4.2 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor P 70 | ------ | PAB | PR * | TL - LONG
TRISPACE 580 | 580 | 498800 | 641.6 | 5.4 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor P 100 | ------ | PAB | PR * | TL - LONG
TRISPACE 650 | 650 | 559000 | 717.4 | 6.6 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor P 100 | ------ | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## IVAR TRINOx
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - TRINOx
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
TRINOx 1000 | 1165 | 1001900 | 1260 | 4.5 | Blu 1700.1 R | PAB | PR * | TC - SHORT | Maior P 150.1 | PAB | PR * | TC - SHORT | Multicalor P 170.1 | PAB | PR * | TC - SHORT
TRINOx 1200 | 1410 | 1212600 | 1522 | 6.6 | Blu 1700.1 | PAB | PR * | TC - SHORT | Maior P 200.1 | PAB | PR * | TC - SHORT | Multicalor P 200.1 | PAB | PR * | TC - SHORT
TRINOx 1500 | 1760 | 1513600 | 1902 | 5.3 | Blu 2000.1 | PAB | PR * | TC - SHORT | Maior P 200.1 | PAB | PR * | TC - SHORT | Multicalor P 200.1 | PAB | PR * | TC - SHORT
TRINOx 1750 | 2040 | 1754400 | 2210 | 5.6 | Blu 3000.1 | ----- | PR * | TC - SHORT | Maior P 300.1 | PAB | PR * | TC - SHORT | Multicalor P 300.1 | PAB | PR * | TC - SHORT
TRINOx 2150 | 2510 | 2158600 | 2710 | 5.6 | Blu 4000.1 | ----- | PR * | TC - SHORT | Maior P 400.1 | PAB | PR * | TC - SHORT | Multicalor P 400.1 | ----- | PR * | TC - SHORT
TRINOx 2580 | 3020 | 2597200 | 3260 | 5.5 | Blu 4000.1 | ----- | PR * | TC - SHORT | Maior P 400.1 | PAB | PR * | TC - SHORT | Multicalor P 400.1 | ----- | PR * | TC - SHORT
TRINOx 3000 | 3520 | 3027200 | 3810 | 7.7 | Blu 5000.1 | ----- | PR * | TC - SHORT | Maior P 500.1 | PAB | PR * | TC - SHORT | Multicalor P 500.1 | ----- | PR * | TC - SHORT
TRINOx 3500 | 4090 | 3517400 | 4420 | 5.4 | Blu 5000.1 | ----- | PR * | TC - SHORT | Maior P 500.1 | PAB | PR * | TC - SHORT | Multicalor P 500.1 | ----- | PR * | TC - SHORT
TRINOx 4000 | 4680 | 4024800 | 5050 | 7 | Blu 6000.1 | ----- | PR * | TC - SHORT | Maior P 600.1 | PAB | PR * | TC - SHORT | Multicalor P 600.1 | ----- | PR * | TC - SHORT
TRINOx 4300 | 5030 | 4325800 | 5450 | 8.2 | Blu 7000.1 | ----- | PR * | STD. | Maior P 700.1 | ----- | PR * | STD. | Multicalor P 700.1 | ----- | PR * | STD.
TRINOx 5000 | 5830 | 5013800 | 6310 | 5.6 | Blu 7000.1 | ----- | PR * | STD. | Maior P 700.1 | ----- | PR * | STD. | Multicalor P 700.1 | ----- | PR * | STD.
TRINOx 6000 | 7020 | 6037200 | 7590 | 8.4 | Blu 8000.1 | ----- | PR * | STD. | Maior P 800.1 | ----- | PR * | STD. | Multicalor P 800.1 | ----- | PR * | STD.
TRINOx 7500 | 8760 | 7533600 | 9460 | 8.1 | Blu 10000.1 | ----- | PR * | STD. | Maior P 1000.1 | ----- | PR * | STD. | Multicalor P 1000.1 | ----- | PR * | STD.
TRINOx 9000 | 10560 | 9081600 | 11400 | 8.7 | Blu 12000.1 | ----- | PR * | STD. | Maior P 1200.1 | ----- | PR * | STD. | Multicalor P 1200.1 | ----- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## IVAR BHP
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - BHP
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
BHP 140 | 97 | 83420 | 107.5 | 1.5 | Max Gas 120 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ----- | TL - LONG | Dual 3 P | P | ----- | ----- | TL - LONG
BHP 200 | 138 | 118680 | 153 | 2 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ----- | TL - LONG | Dual 4 P | P | ----- | ----- | TL - LONG
BHP 300 | 208 | 178880 | 231 | 2.5 | Blu 350 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ----- | TL - LONG | Dual 5 P | P | ----- | ----- | TL - LONG
BHP 400 | 277 | 238220 | 307.5 | 3 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | ----- | PAB | ----- | TL - LONG | Dual 5 P | P | ----- | ----- | TL - LONG
BHP 500 | 346 | 297560 | 384 | 4.2 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ----- | PAB | PR * | TL - LONG | Multicalor P 45 | ----- | PAB | PR * | TL - LONG
BHP 700 | 485 | 417100 | 538.5 | 4.5 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor P 70 | ----- | PAB | PR * | TL - LONG
BHP 800 | 554 | 476440 | 615.5 | 5 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 80 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
BHP 1000 | 692 | 595120 | 768.5 | 6 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
BHP 1250 | 865 | 743900 | 961 | 6.5 | Blu 1400 | ----- | PAB | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor P 140 | ----- | PAB | PR * | TL - LONG
BHP 1500 | 1038 | 892680 | 1153.3 | 6.8 | Blu 1700.1 R | ----- | PAB | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 140 | ----- | PAB | PR * | TL - LONG
BHP 1750 | 1212 | 1042320 | 1346.5 | 7 | Blu 1700.1 R | ----- | PAB | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
BHP 2000 | 1385 | 1191100 | 1538.5 | 7 | Blu 1700.1 | ----- | PAB | PR * | TL - LONG | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
BHP 2500 | 1731 | 1488660 | 1923 | 8 | Blu 3000.1 | ----- | PAB | PR * | TL - LONG | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
BHP 3000 | 2077 | 1786220 | 2307.5 | 8.2 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
BHP 3500 | 2423 | 2083780 | 2692 | 9 | Blu 4000.1 | ----- | ----- | PR * | TL - LONG | Maior P 400.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 400.1 | ----- | PAB | PR * | TL - LONG
BHP 4000 | 2769 | 2381340 | 3076.5 | 10 | Blu 4000.1 | ----- | ----- | PR * | TL - LONG | Maior P 400.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 400.1 | ----- | PAB | PR * | TL - LONG
BHP 5000 | 3463 | 2978180 | 3847 | 10.2 | Blu 5000.1 | ----- | ----- | PR * | TL - LONG | Maior P 500.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 500.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - BHP
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
BHP 140 | 97 | 83420 | 107.5 | 1.5 | Oilflam 15.1 | P | PAB | ----- | TL - LONG | Oilflam 15.1 | P | PAB | ----- | TL - LONG | --------------------- | ----- | ----- | ----- | -----
BHP 200 | 138 | 118680 | 153 | 2 | Oilflam 20.1 | P | PAB | ----- | TL - LONG | Oilflam 20.1 | P | PAB | ----- | TL - LONG | --------------------- | ----- | ----- | ----- | -----
BHP 300 | 208 | 178880 | 231 | 2.5 | Oilflam 30.1 | P | PAB | ----- | TL - LONG | Oilflam 30.1 | P | PAB | ----- | TL - LONG | --------------------- | ----- | ----- | ----- | -----
BHP 400 | 277 | 238220 | 307.5 | 3 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
BHP 500 | 346 | 297560 | 384 | 4.2 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
BHP 700 | 485 | 417100 | 538.5 | 4.5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 70 | ----- | PAB | PR * | TL - LONG
BHP 800 | 554 | 476440 | 615.5 | 5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 70 | ----- | PAB | PR * | TL - LONG
BHP 1000 | 692 | 595120 | 768.5 | 6 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
BHP 1250 | 865 | 743900 | 961 | 6.5 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
BHP 1500 | 1038 | 892680 | 1153.3 | 6.8 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
BHP 1750 | 1212 | 1042320 | 1346.5 | 7 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
BHP 2000 | 1385 | 1191100 | 1538.5 | 7 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Multiflam 200.1 | ----- | PAB | PR * | TL - LONG
BHP 2500 | 1731 | 1488660 | 1923 | 8 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
BHP 3000 | 2077 | 1786220 | 2307.5 | 8.2 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
BHP 3500 | 2423 | 2083780 | 2692 | 9 | Oilflam 400.1 | ----- | PAB | PR * | TL - LONG | Oilflam 400.1 | ----- | PAB | PR * | TL - LONG | Multiflam 400.1 | ----- | PAB | PR * | TL - LONG
BHP 4000 | 2769 | 2381340 | 3076.5 | 10 | Oilflam 400.1 | ----- | PAB | PR * | TL - LONG | Oilflam 400.1 | ----- | PAB | PR * | TL - LONG | Multiflam 400.1 | ----- | PAB | PR * | TL - LONG
BHP 5000 | 3463 | 2978180 | 3847 | 10.2 | Oilflam 500.1 | ----- | PAB | PR * | TL - LONG | Oilflam 500.1 | ----- | PAB | PR * | TL - LONG | Multiflam 500.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## IVAR BLP
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - BLP
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
BLP 140 | 94 | 80840 | 107.5 | 1.5 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | PR * | TL - LONG | Dual 3 P | P | PAB | PR * | TL - LONG
BLP 200 | 134 | 115240 | 153 | 2 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | PR * | TL - LONG | Dual 4 P | P | PAB | PR * | TL - LONG
BLP 300 | 201 | 172860 | 231 | 2.5 | Blu 350 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | PR * | TL - LONG | Dual 5 P | P | PAB | PR * | TL - LONG
BLP 400 | 268 | 230480 | 307.5 | 3 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | PR * | TL - LONG | Dual 5 P | P | PAB | PR * | TL - LONG
BLP 500 | 335 | 288100 | 384 | 4.2 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ----- | PAB | PR * | TL - LONG | Multicalor P 45 | ----- | PAB | PR * | TL - LONG
BLP 700 | 469 | 403340 | 538.5 | 4.5 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ----- | PAB | PR * | TL - LONG | Multicalor P 70 | ----- | PAB | PR * | TL - LONG
BLP 800 | 536 | 460960 | 615.5 | 5 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 80 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
BLP 1000 | 670 | 576200 | 768.5 | 6 | Blu 1000 | ----- | PAB | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor P 100 | ----- | PAB | PR * | TL - LONG
BLP 1250 | 837 | 719820 | 961 | 6.5 | Blu 1400 | ----- | ----- | PR * | TL - LONG | Maior P 120 | ----- | PAB | PR * | TL - LONG | Multicalor P 140 | ----- | PAB | PR * | TL - LONG
BLP 1500 | 1005 | 864300 | 1153.3 | 6.8 | Blu 1700.1 R | ----- | ----- | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 140 | ----- | PAB | PR * | TL - LONG
BLP 1750 | 1172 | 1007920 | 1346.5 | 7 | Blu 1700.1 R | ----- | ----- | PR * | TL - LONG | Maior P 150.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
BLP 2000 | 1339 | 1151540 | 1538.5 | 7 | Blu 1700.1 | ----- | ----- | PR * | TL - LONG | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
BLP 2500 | 1674 | 1439640 | 1923 | 8 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
BLP 3000 | 2009 | 1727740 | 2307.5 | 8.2 | Blu 3000.1 | ----- | ----- | PR * | TL - LONG | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - BHP
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
BLP 140 | 94 | 80840 | 107.5 | 1.5 | Oilflam 15.1 | P | PAB | ----- | TL - LONG | Oilflam 15.1 | P | PAB | ----- | TL - LONG | --------------------- | ----- | ----- | ----- | -----
BLP 200 | 134 | 115240 | 153 | 2 | Oilflam 20.1 | P | PAB | ----- | TL - LONG | Oilflam 20.1 | P | PAB | ----- | TL - LONG | --------------------- | ----- | ----- | ----- | -----
BLP 300 | 201 | 172860 | 231 | 2.5 | Oilflam 30.1 | P | PAB | ----- | TL - LONG | Oilflam 30.1 | P | PAB | ----- | TL - LONG | --------------------- | ----- | ----- | ----- | -----
BLP 400 | 268 | 230480 | 307.5 | 3 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
BLP 500 | 335 | 288100 | 384 | 4.2 | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Oilflam 50.1 | ----- | PAB | PR * | TL - LONG | Multiflam 50 | ----- | PAB | PR * | TL - LONG
BLP 700 | 469 | 403340 | 538.5 | 4.5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 70 | ----- | PAB | PR * | TL - LONG
BLP 800 | 536 | 460960 | 615.5 | 5 | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Oilflam 80.1 | ----- | PAB | PR * | TL - LONG | Multiflam 70 | ----- | PAB | PR * | TL - LONG
BLP 1000 | 670 | 576200 | 768.5 | 6 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
BLP 1250 | 837 | 719820 | 961 | 6.5 | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Oilflam 120.1 | ----- | PAB | PR * | TL - LONG | Multiflam 120 | ----- | PAB | PR * | TL - LONG
BLP 1500 | 1005 | 864300 | 1153.3 | 6.8 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
BLP 1750 | 1172 | 1007920 | 1346.5 | 7 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Multiflam 170.1 | ----- | PAB | PR * | TL - LONG
BLP 2000 | 1339 | 1151540 | 1538.5 | 7 | Oilflam 170.1 | ----- | PAB | PR * | TL - LONG | Oilflam 200.1 | ----- | PAB | PR * | TL - LONG | Multiflam 200.1 | ----- | PAB | PR * | TL - LONG
BLP 2500 | 1674 | 1439640 | 1923 | 8 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
BLP 3000 | 2009 | 1727740 | 2307.5 | 8.2 | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Oilflam 300.1 | ----- | PAB | PR * | TL - LONG | Multiflam 300.1 | ----- | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## IVAR SB-V
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: IVAR - SB/V
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
SB/V 2 | 1385 | 1191100 | 1567 | 3.5 | Blu 1700.1 | ----- | PAB | PR * | TC - SHORT | Maior P 200.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 170.1 | ----- | PAB | PR * | TL - LONG
SB/V 3 | 2077 | 1786220 | 2334 | 5.5 | Blu 3000.1 | ----- | ----- | PR * | TC - SHORT | Maior P 300.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 300.1 | ----- | PAB | PR * | TL - LONG
SB/V 4 | 2769 | 2381340 | 3112 | 6 | Blu 4000.1 | ----- | ----- | PR * | TC - SHORT | Maior P 400.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 400.1 | ----- | ----- | PR * | TL - LONG
SB/V 5 | 3462 | 2977320 | 3891 | 7.5 | Blu 5000.1 | ----- | ----- | PR * | TC - SHORT | Maior P 500.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 500.1 | ----- | ----- | PR * | TL - LONG
SB/V 6 | 4155 | 3573300 | 4668 | 8 | Blu 6000.1 | ----- | ----- | PR * | TC - SHORT | Maior P 600.1 | ----- | PAB | PR * | TL - LONG | Multicalor P 600.1 | ----- | ----- | PR * | TL - LONG
SB/V 7 | 4847 | 4168420 | 5446 | 8.5 | Blu 7000.1 | ----- | ----- | PR * | STD. | Maior P 700.1 | ----- | PAB | PR * | STD. | Multicalor P 700.1 | ----- | ----- | PR * | STD.
SB/V 8 | 5540 | 4764400 | 6266 | 10 | Blu 7000.1 | ----- | ----- | PR * | STD. | Maior P 700.1 | ----- | PAB | PR * | STD. | Multicalor P 700.1 | ----- | ----- | PR * | STD.
SB/V 10 | 6923 | 5953780 | 7780 | 7.5 | Blu 8000.1 | ----- | ----- | PR * | STD. | Maior P 800.1 | ----- | PAB | PR * | STD. | Multicalor P 800.1 | ----- | ----- | PR * | STD.
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
SB/V 2 | 1385 | 1191100 | 1567 | 3.5 | Oilflam 170.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 200.1 | ----- | PAB | PR * | TC - SHORT | Multiflam P 200.1 | ----- | PAB | PR * | TC - SHORT
SB/V 3 | 2077 | 1786220 | 2334 | 5.5 | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 300.1 | ----- | PAB | PR * | TC - SHORT | Multiflam P 300.1 | ----- | PAB | PR * | TC - SHORT
SB/V 4 | 2769 | 2381340 | 3112 | 6 | Oilflam 400.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 400.1 | ----- | PAB | PR * | TC - SHORT | Multiflam P 400.1 | ----- | ----- | PR * | TC - SHORT
SB/V 5 | 3462 | 2977320 | 3891 | 7.5 | Oilflam 500.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 500.1 | ----- | PAB | PR * | TC - SHORT | Multiflam P 500.1 | ----- | ----- | PR * | TC - SHORT
SB/V 6 | 4155 | 3573300 | 4668 | 8 | Oilflam 600.1 | ----- | PAB | PR * | TC - SHORT | Oilflam 600.1 | ----- | PAB | PR * | TC - SHORT | Multiflam P 600.1 | ----- | ----- | PR * | TC - SHORT
SB/V 7 | 4847 | 4168420 | 5446 | 8.5 | Oilflam 700.1 | ----- | ----- | PR * | STD. | Oilflam 700.1 | ----- | ----- | PR * | STD. | Multiflam P 700.1 | ----- | ----- | PR * | STD.
SB/V 8 | 5540 | 4764400 | 6266 | 10 | Oilflam 700.1 | ----- | ----- | PR * | STD. | Oilflam 800.1 | ----- | ----- | PR * | STD. | Multiflam P 700.1 | ----- | ----- | PR * | STD.
SB/V 10 | 6923 | 5953780 | 7780 | 7.5 | Oilflam 800.1 | ----- | ----- | PR * | STD. | Oilflam 800.1 | ----- | ----- | PR * | STD. | Multiflam P 800.1 | ----- | ----- | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE