## KOLVI
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: KOLVI
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
KOLVI 80 | 80 | 68800 | 86 | 0 | Max Gas 105 | P | PAB | ------ | TL - LONG | Max P 8 | P | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TL - LONG
KOLVI 90 | 90 | 77400 | 97 | 0.5 | Max Gas 120 | P | PAB | ------ | TL - LONG | Max P 12 | P | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TL - LONG
KOLVI 120 | 100 | 86000 | 129 | 1.1 | Max Gas 170 | P | PAB | PR * | TL - LONG | Max P 15 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
KOLVI 140 | 140 | 120400 | 151 | 1.1 | Max Gas 250 | P | PAB | PR * | TL - LONG | Max P 25 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
KOLVI 170 | 170 | 146200 | 183 | 2 | Max Gas 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
KOLVI 200 | 200 | 172000 | 215 | 3.1 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
KOLVI 250 | 250 | 215000 | 269 | 3.2 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
KOLVI 270 | 270 | 232200 | 290 | 3.8 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
KOLVI 300 | 300 | 258000 | 323 | 3.6 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
KOLVI 350 | 350 | 301000 | 377 | 4 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
KOLVI 380 | 380 | 326800 | 409 | 4 | Blu 500 | ------ | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
KOLVI 440 | 440 | 378400 | 473 | 5.2 | Blu 700 | ------ | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 70 | ------ | PAB | PR * | TL - LONG
KOLVI 500 | 500 | 430000 | 538 | 5.3 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 70 | ------ | PAB | PR * | TL - LONG
KOLVI 550 | 550 | 473000 | 592 | 5.8 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
KOLVI 600 | 600 | 516000 | 645 | 5.6 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
KOLVI 650 | 650 | 559000 | 700 | 6.7 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
KOLVI 1000 | 1000 | 860000 | 1075 | 6 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 150.1 | ------ | PAB | PR * | TL - LONG | Multicalor 140 | ------ | PAB | PR * | TL - LONG
KOLVI 1300 | 1300 | 1118000 | 1400 | 6.8 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 200.1 | ------ | PAB | PR * | TL - LONG | Multicalor 170.1 | ------ | PAB | PR * | TL - LONG
KOLVI 1500 | 1500 | 1290000 | 1615 | 7.8 | Blu 2000.1 | ------ | PAB | PR * | TL - LONG | Maior P 200.1 | ------ | PAB | PR * | TL - LONG | Multicalor 200.1 | ------ | PAB | PR * | TL - LONG
KOLVI 3000 | 3000 | 2580000 | 3226 | 7.8 | Blu 4000.1 | ------ | ------ | PR * | TL - LONG | Maior P 400.1 | ------ | PAB | PR * | TL - LONG | Multicalor 400.1 | ------ | PAB | PR * | TL - LONG
KOLVI 4500 | 4500 | 3870000 | 4900 | 11.8 | Blu 6000.1 | ------ | ------ | PR * | TL - LONG | Maior P 600.1 | ------ | PAB | PR * | TL - LONG | Multicalor 600.1 | ------ | PAB | PR * | TL - LONG
KOLVI 7000 | 7000 | 6020000 | 7610 | 10 | Blu 8000.1 | ------ | ------ | PR * | STD. | Maior P 800.1 | ------ | ------ | PR * | STD. | Multicalor 800.1 | ------ | PAB | PR * | STD.
KOLVI 10000 | 10000 | 8600000 | 10870 | 16 | Blu 12000.1 | ------ | ------ | PR * | STD. | Maior P 1200.1 | ------ | ------ | PR * | STD. | Multicalor 1200.1 | ------ | PAB | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: KOLVI
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
KOLVI 80 | 80 | 68800 | 86 | 0 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 90 | 90 | 77400 | 97 | 0.5 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 120 | 100 | 86000 | 129 | 1.1 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 140 | 140 | 120400 | 151 | 1.1 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 170 | 170 | 146200 | 183 | 2 | Oilflam 20.1 | P | ------ | ------ | TL - LONG | Oilflam 20.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 200 | 200 | 172000 | 215 | 3.1 | Oilflam 20.1 | P | ------ | ------ | TL - LONG | Oilflam 20.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 250 | 250 | 215000 | 269 | 3.2 | Oilflam 30.1 | P | ------ | ------ | TL - LONG | Oilflam 30.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 270 | 270 | 232200 | 290 | 3.8 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
KOLVI 300 | 300 | 258000 | 323 | 3.6 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
KOLVI 350 | 350 | 301000 | 377 | 4 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
KOLVI 380 | 380 | 326800 | 409 | 4 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
KOLVI 440 | 440 | 378400 | 473 | 5.2 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
KOLVI 500 | 500 | 430000 | 538 | 5.3 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
KOLVI 550 | 550 | 473000 | 592 | 5.8 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
KOLVI 600 | 600 | 516000 | 645 | 5.6 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
KOLVI 650 | 650 | 559000 | 700 | 6.7 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
KOLVI 1000 | 1000 | 860000 | 1075 | 6 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
KOLVI 1300 | 1300 | 1118000 | 1400 | 6.8 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 170.1 | ------ | PAB | PR * | TL - LONG
KOLVI 1500 | 1500 | 1290000 | 1615 | 7.8 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 200.1 | ------ | PAB | PR * | TL - LONG
KOLVI 3000 | 3000 | 2580000 | 3226 | 7.8 | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Multiflam 400.1 | ------ | PAB | PR * | TL - LONG
KOLVI 4500 | 4500 | 3870000 | 4900 | 11.8 | Oilflam 600.1 | ------ | PAB | PR * | TL - LONG | Oilflam 600.1 | ------ | PAB | PR * | TL - LONG | Multiflam 600.1 | ------ | PAB | PR * | TL - LONG
KOLVI 7000 | 7000 | 6020000 | 7610 | 10 | Oilflam 800.1 | ------ | ------ | PR * | STD. | Oilflam 800.1 | ------ | ------ | PR * | STD. | Multiflam 800.1 | ------ | PAB | PR * | STD.
KOLVI 10000 | 10000 | 8600000 | 10870 | 16 | Oilflam 1200.1 | ------ | ------ | PR * | STD. | Oilflam 1200.1 | ------ | ------ | PR * | STD. | Multiflam 1200.1 | ------ | PAB | PR * | STD.
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## KOLVI Ukraine
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: KOLVI
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
KOLVI 80 | 93 | 79980 | 100 | 0.5 | Max Gas 105 | P | PAB | ------ | TL - LONG | Max P 8 | P | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TL - LONG
KOLVI 90 | 99 | 85140 | 106.4516 | 0.5 | Max Gas 120 | P | PAB | ------ | TL - LONG | Max P 12 | P | ------ | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TL - LONG
KOLVI 120 | 140 | 120400 | 150.5376 | 1.1 | Max Gas 170 | P | PAB | PR * | TL - LONG | Max P 15 | P | PAB | ------ | TL - LONG | Dual 3 P | P | ------ | ------ | TL - LONG
KOLVI 140 | 163 | 140180 | 175.2688 | 1.1 | Max Gas 250 | P | PAB | PR * | TL - LONG | Max P 25 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
KOLVI 170 | 198 | 170280 | 212.9032 | 2 | Max Gas 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
KOLVI 200 | 233 | 200380 | 250.5376 | 3.1 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
KOLVI 250 | 291 | 250260 | 312.9032 | 3.2 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
KOLVI 270 | 314 | 270040 | 337.6344 | 3.8 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
KOLVI 300 | 349 | 300140 | 375.2688 | 3.6 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
KOLVI 350 | 407 | 350020 | 437.6344 | 4 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
KOLVI 440 | 512 | 440320 | 550.5376 | 5.2 | Blu 700 | ------ | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 70 | ------ | PAB | PR * | TL - LONG
KOLVI 500 | 581 | 499660 | 624.7312 | 5.3 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 70 | ------ | PAB | PR * | TL - LONG
KOLVI 550 | 640 | 550400 | 688.172 | 5.8 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
KOLVI 600 | 698 | 600280 | 750.5376 | 5.6 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
KOLVI 650 | 756 | 650160 | 812.9032 | 6.7 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
KOLVI 1000 | 1100 | 946000 | 1182.7957 | 6 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 150.1 | ------ | PAB | PR * | TL - LONG | Multicalor 140 | ------ | PAB | PR * | TL - LONG
KOLVI 1300 | 1300 | 1118000 | 1397.8495 | 6.8 | Blu 1700.1 R | ------ | PAB | PR * | TL - LONG | Maior P 200.1 | ------ | PAB | PR * | TL - LONG | Multicalor 170.1 | ------ | PAB | PR * | TL - LONG
KOLVI 1500 | 1500 | 1290000 | 1612.9032 | 7.8 | Blu 2000.1 | ------ | PAB | PR * | TL - LONG | Maior P 200.1 | ------ | PAB | PR * | TL - LONG | Multicalor 200.1 | ------ | PAB | PR * | TL - LONG
KOLVI 3000 | 3000 | 2580000 | 3225.8065 | 7.8 | Blu 4000.1 | ------ | PAB | PR * | TL - LONG | Maior P 400.1 | ------ | PAB | PR * | TL - LONG | Multicalor 400.1 | ------ | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: KOLVI
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
KOLVI 80 | 93 | 79980 | 100 | 0.5 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 90 | 99 | 85140 | 106.4516 | 0.5 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 120 | 140 | 120400 | 150.5376 | 1.1 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 140 | 163 | 140180 | 175.2688 | 1.1 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 170 | 198 | 170280 | 212.9032 | 2 | Oilflam 20.1 | P | ------ | ------ | TL - LONG | Oilflam 20.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 200 | 233 | 200380 | 250.5376 | 3.1 | Oilflam 20.1 | P | ------ | ------ | TL - LONG | Oilflam 20.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 250 | 291 | 250260 | 312.9032 | 3.2 | Oilflam 30.1 | P | ------ | ------ | TL - LONG | Oilflam 30.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
KOLVI 270 | 314 | 270040 | 337.6344 | 3.8 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
KOLVI 300 | 349 | 300140 | 375.2688 | 3.6 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
KOLVI 350 | 407 | 350020 | 437.6344 | 4 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
KOLVI 440 | 512 | 440320 | 550.5376 | 5.2 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
KOLVI 500 | 581 | 499660 | 624.7312 | 5.3 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
KOLVI 550 | 640 | 550400 | 688.172 | 5.8 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
KOLVI 600 | 698 | 600280 | 750.5376 | 5.6 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
KOLVI 650 | 756 | 650160 | 812.9032 | 6.7 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
KOLVI 1000 | 1100 | 946000 | 1182.7957 | 6 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
KOLVI 1300 | 1300 | 1118000 | 1397.8495 | 6.8 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 170.1 | ------ | PAB | PR * | TL - LONG
KOLVI 1500 | 1500 | 1290000 | 1612.9032 | 7.8 | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Oilflam 170.1 | ------ | PAB | PR * | TL - LONG | Multiflam 200.1 | ------ | PAB | PR * | TL - LONG
KOLVI 3000 | 3000 | 2580000 | 3225.8065 | 7.8 | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Multiflam 400.1 | ------ | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE