## VITOPLEX 100 SX1
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 SX1
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 100 SX1 | 80 | 68800 | 87 | 0.45 | Max Gas 105 | P | PAB | PR * | TC - SHORT | Max P 8 | P | ------ | ------ | TC - SHORT | Dual 3 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 90 | 77400 | 99 | 0.57 | Max Gas 105 | P | PAB | PR * | TC - SHORT | Max P 8 | P | ------ | ------ | TC - SHORT | Dual 3 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 105 | 90300 | 115 | 0.6 | Max Gas 120 | P | PAB | PR * | TC - SHORT | Max P 12 | P | ------ | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 115 | 98900 | 126 | 0.72 | Max Gas 170 | P | PAB | PR * | TC - SHORT | Max P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 130 | 111800 | 142 | 0.65 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 145 | 124700 | 159 | 0.81 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 170 | 146200 | 186 | 0.9 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 190 | 163400 | 209 | 1.1 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 SX1 | 225 | 193500 | 245 | 1.2 | Blu 350 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 250 | 215000 | 273 | 1.5 | Blu 350 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 285 | 245100 | 310 | 2 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | PAB | ------ | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 315 | 270900 | 344 | 2.4 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 345 | 296700 | 375 | 2.1 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 380 | 326800 | 415 | 2.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 405 | 348300 | 440 | 2.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 445 | 382700 | 486 | 3 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 460 | 395600 | 500 | 2.7 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 500 | 430000 | 546 | 3.2 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 575 | 494500 | 625 | 3 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 635 | 546100 | 694 | 3.3 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 720 | 619200 | 782 | 3.5 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 790 | 679400 | 863 | 4.2 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 895 | 769700 | 972 | 3.6 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 985 | 847100 | 1076 | 4.4 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1120 | 963200 | 1217 | 5.2 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1230 | 1057800 | 1344 | 6.3 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1400 | 1204000 | 1522 | 4.7 | Blu 1700.1 | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1540 | 1324400 | 1683 | 5.7 | Blu 2000.1 | ------ | PAB | PR * | TC - SHORT | Maior P 200.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 200.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1750 | 1505000 | 1902 | 5 | Blu 2000.1 | ------ | PAB | PR * | TC - SHORT | Maior P 200.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 SX1
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 100 SX1 | 80 | 68800 | 87 | 0.45 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 90 | 77400 | 99 | 0.57 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 105 | 90300 | 115 | 0.6 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 115 | 98900 | 126 | 0.72 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 130 | 111800 | 142 | 0.65 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 145 | 124700 | 159 | 0.81 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 170 | 146200 | 186 | 0.9 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 190 | 163400 | 209 | 1.1 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 225 | 193500 | 245 | 1.2 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 250 | 215000 | 273 | 1.5 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 285 | 245100 | 310 | 2 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 SX1 | 315 | 270900 | 344 | 2.4 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 345 | 296700 | 375 | 2.1 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 380 | 326800 | 415 | 2.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 405 | 348300 | 440 | 2.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 445 | 382700 | 486 | 3 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 460 | 395600 | 500 | 2.7 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 500 | 430000 | 546 | 3.2 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 575 | 494500 | 625 | 3 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 635 | 546100 | 694 | 3.3 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 720 | 619200 | 782 | 3.5 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 790 | 679400 | 863 | 4.2 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 895 | 769700 | 972 | 3.6 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 985 | 847100 | 1076 | 4.4 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1120 | 963200 | 1217 | 5.2 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1230 | 1057800 | 1344 | 6.3 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1400 | 1204000 | 1522 | 4.7 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1540 | 1324400 | 1683 | 5.7 | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 200.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1750 | 1505000 | 1902 | 5 | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VITOPLEX 100 PX1
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 PX1
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 100 PX1 | 125 | 107500 | 136 | 0.61 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | ------ | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 140 | 120400 | 153 | 0.61 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | ------ | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 150 | 129000 | 163 | 0.8 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | ------ | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 165 | 141900 | 180 | 0.8 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | ------ | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 190 | 163400 | 207 | 0.9 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 210 | 180600 | 229 | 0.9 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 240 | 206400 | 261 | 1.2 | Blu 350 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | ------ | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 265 | 227900 | 290 | 1.2 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | ------ | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 310 | 266600 | 337 | 2 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | PAB | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 PX1 | 340 | 292400 | 372 | 2 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | P | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 400 | 344000 | 435 | 2.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | P | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 440 | 378400 | 481 | 2.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 60 | P | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 500 | 430000 | 543 | 2.7 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | P | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 550 | 473000 | 601 | 2.7 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | P | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 PX1
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 100 PX1 | 125 | 107500 | 136 | 0.61 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 140 | 120400 | 153 | 0.61 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 150 | 129000 | 163 | 0.8 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 165 | 141900 | 180 | 0.8 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 190 | 163400 | 207 | 0.9 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 210 | 180600 | 229 | 0.9 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 240 | 206400 | 261 | 1.2 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 265 | 227900 | 290 | 1.2 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 PX1 | 310 | 266600 | 337 | 2 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 340 | 292400 | 372 | 2 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 400 | 344000 | 435 | 2.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 440 | 378400 | 481 | 2.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 500 | 430000 | 543 | 2.7 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 PX1 | 550 | 473000 | 601 | 2.7 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VITOPLEX 100 LS
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 LS
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 100 LS | 170 | 146200 | 186 | 0.9 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 LS | 285 | 245100 | 311 | 1.8 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | PAB | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 100 LS | 460 | 395600 | 503 | 2.5 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 LS | 580 | 498800 | 634 | 3 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 LS | 900 | 774000 | 984 | 3.6 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 LS | 1450 | 1247000 | 1585 | 4.7 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 LS
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 100 LS | 170 | 146200 | 186 | 0.9 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 LS | 285 | 245100 | 311 | 1.8 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 100 LS | 460 | 395600 | 503 | 2.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 LS | 580 | 498800 | 634 | 3 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 LS | 900 | 774000 | 984 | 3.6 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 LS | 1450 | 1247000 | 1585 | 4.7 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VITOPLEX 200 SX2
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 200 SX2
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 200 SX2 | 90 | 77400 | 98 | 0.6 | Max Gas 105 | P | PAB | PR * | TC - SHORT | Max P 8 | P | ------ | ------ | TC - SHORT | Dual 3 P | P | ------ | ------ | TC - SHORT
VITOPLEX 200 SX2 | 120 | 103200 | 130 | 0.8 | Max Gas 170 | P | PAB | PR * | TC - SHORT | Max P 12 | P | ------ | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 200 SX2 | 150 | 129000 | 163 | 1 | Max Gas 250 | P | PAB | PR * | TC - SHORT | Max P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 200 SX2 | 200 | 172000 | 217 | 2 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 200 SX2 | 270 | 232200 | 293 | 1.8 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | PAB | ------ | TC - SHORT | Dual 5 P | P | ------ | ------ | TC - SHORT
VITOPLEX 200 SX2 | 350 | 301000 | 380 | 3.1 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | P | PAB | ------ | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 200 SX2 | 440 | 378400 | 478 | 2.8 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 45 | P | PAB | ------ | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 200 SX2 | 560 | 481600 | 609 | 4 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | P | PAB | ------ | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 SX1
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 200 SX2 | 90 | 77400 | 98 | 0.6 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 200 SX2 | 120 | 103200 | 130 | 0.8 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 200 SX2 | 150 | 129000 | 163 | 1 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 200 SX2 | 200 | 172000 | 217 | 2 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 200 SX2 | 270 | 232200 | 293 | 1.8 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 200 SX2 | 350 | 301000 | 380 | 3.1 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 200 SX2 | 440 | 378400 | 478 | 2.8 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 200 SX2 | 560 | 481600 | 609 | 4 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VITOPLEX 300 TX3
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 300 TX3
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 300 TX3 | 80 | 68800 | 87 | 0.45 | Max Gas 105 | P | PAB | PR * | TC - SHORT | Max P 8 | P | ------ | ------ | TC - SHORT | Dual 3 P | P | ------ | ------ | TC - SHORT
VITOPLEX 300 TX3 | 105 | 90300 | 115 | 0.6 | Max Gas 120 | P | PAB | PR * | TC - SHORT | Max P 12 | P | ------ | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 300 TX3 | 130 | 111800 | 142 | 0.65 | Max Gas 170 | P | PAB | PR * | TC - SHORT | MAX P 15 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 300 TX3 | 170 | 146200 | 186 | 0.9 | Max Gas 250 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 4 P | P | ------ | ------ | TC - SHORT
VITOPLEX 300 TX3 | 225 | 193500 | 245 | 1.2 | Blu 350 | P | PAB | PR * | TC - SHORT | MAX P 25 | P | PAB | ------ | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
VITOPLEX 300 TX3 | 285 | 245100 | 310 | 2 | Blu 350 | P | PAB | PR * | TC - SHORT | Maior P 35 | P | PAB | ------ | TC - SHORT | Dual 5 P | ------ | PAB | PR * | TC - SHORT
VITOPLEX 300 TX3 | 345 | 296700 | 375 | 2.1 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 300 TX3 | 405 | 348300 | 440 | 2.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 300 TX3 | 460 | 395600 | 500 | 2.7 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 575 | 494500 | 625 | 3 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 720 | 619200 | 782 | 3.5 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 895 | 769700 | 972 | 3.6 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1120 | 963200 | 1217 | 5.2 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1400 | 1204000 | 1522 | 4.7 | Blu 1700.1 | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1750 | 1505000 | 1902 | 5 | Blu 2000.1 | ------ | PAB | PR * | TC - SHORT | Maior P 200.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 300 TX3
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOPLEX 300 TX3 | 80 | 68800 | 87 | 0.45 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 300 TX3 | 105 | 90300 | 115 | 0.6 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 300 TX3 | 130 | 111800 | 142 | 0.65 | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | Oilflam 15.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 300 TX3 | 170 | 146200 | 186 | 0.9 | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | Oilflam 20.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 300 TX3 | 225 | 193500 | 245 | 1.2 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 300 TX3 | 285 | 245100 | 310 | 2 | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | Oilflam 30.1 | P | ------ | ------ | TC - SHORT | ---------- | ------ | ------ | ------ | ------
VITOPLEX 300 TX3 | 345 | 296700 | 375 | 2.1 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 300 TX3 | 405 | 348300 | 440 | 2.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 300 TX3 | 460 | 395600 | 500 | 2.7 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 575 | 494500 | 625 | 3 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 720 | 619200 | 782 | 3.5 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 895 | 769700 | 972 | 3.6 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1120 | 963200 | 1217 | 5.2 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1400 | 1204000 | 1522 | 4.7 | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 170.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
VITOPLEX 100 SX1 | 1750 | 1505000 | 1902 | 5 | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 200.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VITOROND 200 VD2
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOROND 200 VD2
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOROND 200 VD2 | 320 | 275200 | 348 | 0.5 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 380 | 326800 | 413 | 0.9 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 45 | ------ | PAB | PR * | TC - SHORT | Multicalor 45 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 440 | 378400 | 478 | 1.3 | Blu 500 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 500 | 430000 | 543 | 1.7 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 560 | 481600 | 609 | 1.9 | Blu 700 | P | PAB | PR * | TC - SHORT | Maior P 60 | ------ | PAB | PR * | TC - SHORT | Multicalor 70 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 630 | 541800 | 685 | 2.1 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 700 | 602000 | 761 | 2.8 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 780 | 670800 | 848 | 3.9 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 860 | 739600 | 935 | 4.9 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 950 | 817000 | 1033 | 4.5 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 1080 | 928800 | 1174 | 5.8 | Blu 1700.1 R | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOROND 200 VD2
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOROND 200 VD2 | 320 | 275200 | 348 | 0.5 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 380 | 326800 | 413 | 0.9 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 440 | 378400 | 478 | 1.3 | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 50.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 50.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 500 | 430000 | 543 | 1.7 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 560 | 481600 | 609 | 1.9 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 70.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 630 | 541800 | 685 | 2.1 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 700 | 602000 | 761 | 2.8 | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 780 | 670800 | 848 | 3.9 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 860 | 739600 | 935 | 4.9 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 950 | 817000 | 1033 | 4.5 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOROND 200 VD2 | 1080 | 928800 | 1174 | 5.8 | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 170.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VITOMAX 100 M155
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOMAX 100 M155
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOMAX 100 M155 | 650 | 559000 | 710 | 2 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Maior P 80 | ------ | PAB | PR * | TC - SHORT | Multicalor 100 | ------ | PAB | PR * | TC - SHORT
VITOMAX 100 M155 | 1000 | 860000 | 1090 | 3.4 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Maior P 120 | ------ | PAB | PR * | TC - SHORT | Multicalor 140 | ------ | PAB | PR * | TC - SHORT
VITOMAX 100 M155 | 1400 | 1204000 | 1530 | 4.7 | Blu 1700.1 | ------ | PAB | PR * | TC - SHORT | Maior P 150.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 170.1 | ------ | PAB | PR * | TC - SHORT
VITOMAX 100 M155 | 2000 | 1720000 | 2185 | 6 | Blu 2000.1 | ------ | PAB | PR * | TC - SHORT | Maior P 200.1 | ------ | PAB | PR * | TC - SHORT | Multicalor 200.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOPLEX 100 SX1
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
VITOMAX 100 M155 | 650 | 559000 | 710 | 2 | Blu 1000 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOMAX 100 M155 | 1000 | 860000 | 1090 | 3.4 | Blu 1400 | ------ | PAB | PR * | TC - SHORT | Oilflam 80.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOMAX 100 M155 | 1400 | 1204000 | 1530 | 4.7 | Blu 1700.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
VITOMAX 100 M155 | 2000 | 1720000 | 2185 | 6 | Blu 2000.1 | ------ | PAB | PR * | TC - SHORT | Oilflam 120.1 | ------ | PAB | PR * | TC - SHORT | Multiflam 120.1 | ------ | PAB | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE

## VITOMAX 200 M241
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOMAX 200 M241
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  | LIGHT OIL BURNER |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
VITOMAX 200 M241 | 2100 | 1806000 | 2280 | 5.5 | Blu 3000.1 | ------ | PR * | TC - SHORT | Maior P 300.1 | PAB | PR * | TC - SHORT | Multicalor 300.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 2600 | 2236000 | 2830 | 7 | Blu 4000.1 | ------ | PR * | TC - SHORT | Maior P 400.1 | PAB | PR * | TC - SHORT | Multicalor 400.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 3200 | 2752000 | 3480 | 10 | Blu 5000.1 | ------ | PR * | TC - SHORT | Maior P 500.1 | PAB | PR * | TC - SHORT | Multicalor 500.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 3900 | 3354000 | 4240 | 12.5 | Blu 6000.1 | ------ | PR * | TC - SHORT | Maior P 600.1 | PAB | PR * | TC - SHORT | Multicalor 600.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 4500 | 3870000 | 4890 | 13 | Blu 6000.1 | ------ | PR * | TC - SHORT | Maior P 600.1 | PAB | PR * | TC - SHORT | Multicalor 600.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 5300 | 4558000 | 5760 | 14.5 | Blu 7000.1 | ------ | PR * | TC - SHORT | Maior P 700.1 | ------ | PR * | TC - SHORT | Multicalor 700.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 6600 | 5676000 | 7170 | 16.5 | Blu 8000.1 | ------ | PR * | TC - SHORT | Maior P 800.1 | ------ | PR * | TC - SHORT | Multicalor 800.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 7800 | 6708000 | 8480 | 17.5 | Blu 10000.1 | ------ | PR * | TC - SHORT | Maior P 1000.1 | ------ | PR * | TC - SHORT | Multicalor 1000.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 9300 | 7998000 | 10110 | 19.5 | Blu 12000.1 | ------ | PR * | TC - SHORT | Maior P 1200.1 | ------ | PR * | TC - SHORT | Multicalor 1200.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 11200 | 9632000 | 12170 | 15 | Blu 15000.1 | ------ | PR * | TC - SHORT | Maior P 1500.1 | ------ | PR * | TC - SHORT | Multicalor 1500.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 13800 | 11868000 | 14990 | 15.5 | Blu 15000.1 | ------ | PR * | TC - SHORT | Maior P 1500.1 | ------ | PR * | TC - SHORT | Multicalor 1500.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 15000 | 12900000 | 16300 | 16 | Blu 15000.1 | ------ | PR * | TC - SHORT | Maior P 1500.1 | ------ | PR * | TC - SHORT | Multicalor 1500.1 | ------ | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: VIESSMAN - VITOMAX 200 M241
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE | MODEL | HI LOW | PR MD | BLAST TUBE
VITOMAX 200 M241 | 2100 | 1806000 | 2280 | 5.5 | Oilflam 300.1 | PAB | PR * | TC - SHORT | Oilflam 300.1 | PAB | PR * | TC - SHORT | Multiflam 300.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 2600 | 2236000 | 2830 | 7 | Oilflam 400.1 | PAB | PR * | TC - SHORT | Oilflam 400.1 | PAB | PR * | TC - SHORT | Multiflam 400.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 3200 | 2752000 | 3480 | 10 | Oilflam 500.1 | PAB | PR * | TC - SHORT | Oilflam 500.1 | PAB | PR * | TC - SHORT | Multiflam 500.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 3900 | 3354000 | 4240 | 12.5 | Oilflam 600.1 | PAB | PR * | TC - SHORT | Oilflam 600.1 | PAB | PR * | TC - SHORT | Multiflam 600.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 4500 | 3870000 | 4890 | 13 | Oilflam 600.1 | PAB | PR * | TC - SHORT | Oilflam 600.1 | PAB | PR * | TC - SHORT | Multiflam 600.1 | PAB | PR * | TC - SHORT
VITOMAX 200 M241 | 5300 | 4558000 | 5760 | 14.5 | Oilflam 700.1 | ------ | PR * | TC - SHORT | Oilflam 700.1 | ------ | PR * | TC - SHORT | Multiflam 700.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 6600 | 5676000 | 7170 | 16.5 | Oilflam 800.1 | ------ | PR * | TC - SHORT | Oilflam 800.1 | ------ | PR * | TC - SHORT | Multiflam 800.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 7800 | 6708000 | 8480 | 17.5 | Oilflam 1000.1 | ------ | PR * | TC - SHORT | Oilflam 1000.1 | ------ | PR * | TC - SHORT | Multiflam 1000.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 9300 | 7998000 | 10110 | 19.5 | Oilflam 1200.1 | ------ | PR * | TC - SHORT | Oilflam 1200.1 | ------ | PR * | TC - SHORT | Multiflam 1200.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 11200 | 9632000 | 12170 | 15 | Oilflam 1500.1 | ------ | PR * | TC - SHORT | Oilflam 1500.1 | ------ | PR * | TC - SHORT | Multiflam 1500.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 13800 | 11868000 | 14990 | 15.5 | Oilflam 1500.1 | ------ | PR * | TC - SHORT | Oilflam 1500.1 | ------ | PR * | TC - SHORT | Multiflam 1500.1 | ------ | PR * | TC - SHORT
VITOMAX 200 M241 | 15000 | 12900000 | 16300 | 16 | Oilflam 1500.1 | ------ | PR * | TC - SHORT | Oilflam 1500.1 | ------ | PR * | TC - SHORT | Multiflam 1500.1 | ------ | PR * | TC - SHORT
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE