## ZIOSAB
ECOFLAM S.p.A. BOILERS - BURNERS MATCHING TABLE
BOILER: ZIOSAB - КОТЕЛ ЗИОСАБ
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | GAS BURNER |  |  |  |  | LIGHT OIL BURNER |  |  |  |  | DUAL FUEL BURNER LIGHT OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
ЗИОСАБ - 30M | 30 | 25800 | 33.3333 | 0.25 | Max Gas 40 | P | ------ | ------ | TL - LONG | MAX 1 | ------ | ------ | ------ | TL - LONG | Dual 1 | ------ | ------ | ------ | TL - LONG
ЗИОСАБ - 45 | 45 | 38700 | 50 | 1 | Max Gas 70 | P | ------ | ------ | TL - LONG | MAX 4 | ------ | ------ | ------ | TL - LONG | Dual 2 | ------ | ------ | ------ | TL - LONG
ЗИОСАБ - 125 | 125 | 107500 | 138.8889 | 1 | Max Gas 170 | P | PAB | PR * | TL - LONG | MAX P 15 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
ЗИОСАБ - 175 | 175 | 150500 | 194.4444 | 1.2 | Max Gas 250 | P | PAB | PR * | TL - LONG | MAX P 25 | P | PAB | ------ | TL - LONG | Dual 4 P | P | ------ | ------ | TL - LONG
ЗИОСАБ - 250 | 250 | 215000 | 277.7778 | 1.2 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
ЗИОСАБ - 250M | 250 | 215000 | 277.7778 | 1.2 | Blu 350 | P | PAB | PR * | TL - LONG | Maior P 35 | P | PAB | ------ | TL - LONG | Dual 5 P | P | ------ | ------ | TL - LONG
ЗИОСАБ - 350 | 350 | 301000 | 384.6154 | 2 | Blu 500 | P | PAB | PR * | TL - LONG | Maior P 45 | ------ | PAB | PR * | TL - LONG | Multicalor 45 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 500 | 500 | 430000 | 549.4505 | 2 | Blu 700 | P | PAB | PR * | TL - LONG | Maior P 60 | ------ | PAB | PR * | TL - LONG | Multicalor 70 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 750 | 750 | 645000 | 819.6721 | 4 | Blu 1000 | ------ | PAB | PR * | TL - LONG | Maior P 80 | ------ | PAB | PR * | TL - LONG | Multicalor 100 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 1000 | 1000 | 860000 | 1092.8962 | 4 | Blu 1400 | ------ | PAB | PR * | TL - LONG | Maior P 120 | ------ | PAB | PR * | TL - LONG | Multicalor 140 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 1600 | 1600 | 1376000 | 1739.1304 | 6.5 | Blu 2000.1 | ------ | PAB | PR * | TL - LONG | Maior P 200 | ------ | PAB | PR * | TL - LONG | Multicalor 200.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 2000 | 2000 | 1720000 | 2173.913 | 6.5 | Blu 3000.1 | ------ | PAB | PR * | TL - LONG | Maior P 300 | ------ | PAB | PR * | TL - LONG | Multicalor 300.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 2500 | 2500 | 2150000 | 2717.3913 | 9 | Blu 3000.1 | ------ | PAB | PR * | TL - LONG | Maior P 300 | ------ | PAB | PR * | TL - LONG | Multicalor 300.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 3000 | 3000 | 2580000 | 3260.8696 | 9 | Blu 4000.1 | ------ | PAB | PR * | TL - LONG | Maior P 400 | ------ | PAB | PR * | TL - LONG | Multicalor 400.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 5000 | 5000 | 4300000 | 5434.7826 | 9 | Blu 6000.1 | ------ | PAB | PR * | TL - LONG | Maior P 600 | ------ | PAB | PR * | TL - LONG | Multicalor 600.1 | ------ | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE
TYPE | BOILER OUTPUT Kw | BOILER OUTPUT kcal/h | BOILER INPUT Kw | back pressure mbar | HEAVY OIL BURNER MAX 50° E at 50° C |  |  |  |  | HEAVY OIL BURNER OVER 50° E at 50° C |  |  |  |  | DUAL FUEL BURNER HEAVY OIL - GAS
[5 empty] | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE | MODEL | ON OFF | HI LOW | PR MD | BLAST TUBE
ЗИОСАБ - 30M | 30 | 25800 | 33.3333 | 0.25 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
ЗИОСАБ - 45 | 45 | 38700 | 50 | 1 | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------ | ---------- | ------ | ------ | ------ | ------
ЗИОСАБ - 125 | 125 | 107500 | 138.8889 | 1 | Oilflam 15.1 | P | ------ | ------ | TL - LONG | Oilflam 15.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
ЗИОСАБ - 175 | 175 | 150500 | 194.4444 | 1.2 | Oilflam 20.1 | P | ------ | ------ | TL - LONG | Oilflam 20.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
ЗИОСАБ - 250 | 250 | 215000 | 277.7778 | 1.2 | Oilflam 30.1 | P | ------ | ------ | TL - LONG | Oilflam 30.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
ЗИОСАБ - 250M | 250 | 215000 | 277.7778 | 1.2 | Oilflam 30.1 | P | ------ | ------ | TL - LONG | Oilflam 30.1 | P | ------ | ------ | TL - LONG | ---------- | ------ | ------ | ------ | ------
ЗИОСАБ - 350 | 350 | 301000 | 388.8889 | 2 | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Oilflam 50.1 | ------ | PAB | PR * | TL - LONG | Multiflam 50 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 500 | 500 | 430000 | 555.5556 | 2 | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Oilflam 80.1 | ------ | PAB | PR * | TL - LONG | Multiflam 70 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 750 | 750 | 645000 | 833.3333 | 4 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 1000 | 1000 | 860000 | 1111.1111 | 4 | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Oilflam 120.1 | ------ | PAB | PR * | TL - LONG | Multiflam 120 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 1600 | 1600 | 1376000 | 1777.7778 | 6.5 | Oilflam 200.1 | ------ | PAB | PR * | TL - LONG | Oilflam 200.1 | ------ | PAB | PR * | TL - LONG | Multiflam 200.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 2000 | 2000 | 1720000 | 2222.2222 | 6.5 | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Multiflam 300.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 2500 | 2500 | 2150000 | 2777.7778 | 9 | Oilflam 300.1 | ------ | PAB | PR * | TL - LONG | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Multiflam 400.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 3000 | 3000 | 2580000 | 3333.3333 | 9 | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Oilflam 400.1 | ------ | PAB | PR * | TL - LONG | Multiflam 300.1 | ------ | PAB | PR * | TL - LONG
ЗИОСАБ - 5000 | 5000 | 4300000 | 5555.5556 | 9 | Oilflam 600.1 | ------ | PAB | PR * | TL - LONG | Oilflam 600.1 | ------ | PAB | PR * | TL - LONG | Multiflam 600.1 | ------ | PAB | PR * | TL - LONG
PR * - FOR MD FULL MODULATING VERSION ADD THE PID CONTROLLER RWF 40 + MATCHING PROBE